## Input
Input Data EN 15316-2
Product technical input data list
temperature variation based on control | Dqctr | 0 | K
temperature variation based on control (standard calculation) | Dqcrt,1 | 0 | K
temperature variation based on control (certified products) | Dqcrt,2 | 0.7 | K
hysteresis of thermostatic valve | qH | 0 | K
water temperature effect of thermostatic valve | qW | 0 | K
temperature variation based on intermittent controls operation system | Dqim;crt | 0 | K
temperature variation based on intermittent operation of the emission system | Dqim;emt | 0 | K
temperature variation based on radiation by type of the emission system | Dqrad | 0 | K
temperature variation based on stratification | Dqstr | 0 | K
temperature variation based on stratification (over-temperature dependend) | Dqstr,1 | 0.7 | K
temperature variation based on stratification (specific heat losses via external components) | Dqstr,2 | 0.5 | K
air temperature gradient für rooms with ceillings heights ≥4m | q'str | 0 | K/m
temperature variation based on an additional heat loss by emitters embedded in the envelope | Dqemb | 0 | K
| Dqemb,1 | 0 | K
| Dqemb,2 | 0 | K
temperature variation based on all the influences Dq=Dqctr+Dqstr+Dqemb | Dq | 0 | K
temperature variation based on not balanced hydraulic systems | Dqhydr | 0 | K
temperature variation based on room atomization | Dqroomout | 0 | K
radiant factor of radiant heaters for room heights ≥ 4m | RF | 0 | -
room height | hR | 2.5 | m
Electrical rated power consumption of the control | Pctr | 0 | W
Electrical rated power consumption of the equipment | PH,aux | 0 | W
Electrical rated power consumption of the fan | Pfan | 0 | W
Configuration and system design data
design over-temperature |  | 0 | K
number of the ventilators / fan units | nfan | 0 | -
Operating conditions data list
initial internal temperature | qi,ini | 20 | K
calculation interval | tci | 0 | h
total time of generator(s) operation | tgnr | 0 | h
external temperature of the calculation interval | qe,avg | 10 | °C
Temperature variation for consideration of solar and internal gains | Dqe,sol | 0 | K
Thermal output of the heat emission system | Qem;out | 100 | kWh
operation time of the fans in the calculation period | th,rl | 0 | h
is the monthly or other period analytical running time | th | 0 | h

## Calculation
Calculation Data EN 15316-2
Energy calculation (additional heat losses)
Control |  | Dqctr= CA | CA=0,45*(qW+qH) | 0 | K
|  | Dqctr,1 |  | 0 | K
|  | Dqctr,2 |  | 0.7 | K
|  | Dqctr |  | 0.7 | K
Stratification | h< 4 m | Dqstr | Dqstr=(Dqstr,1+Dqstr,2)/2 | 0.6 | K
|  | Dqstr |  | 0 | K
|  | Dqstr |  | 0.6 | K
| h> 4 m | Dqstr | Dqstr=(10*q'str/16)*(0,5*hR-1,1) | 0 | K
|  | Dqstr |  | 0.6 | K
Radiation | h< 4 m | Dqrad |  | 0 | K
| h> 4 m | Dqrad | Dqrad=10*((0,36/(RF+0,2))+0,354*(10/hR)^(0,15)-0,9) | 13.3583 | K
|  | Dqrad |  | 0 | K
Embedded |  | Dqemb | Dqemb=(Dqemb,1+Dqemb,2)/2 | 0 | K
|  | Dqemb |  | 0 | K
|  | Dqemb |  | 0 | K
Intermittent Operation |  | Dqim | Dqim=Dqim,emt + Dqim,ctr | 0 | K
Hydraulic |  | Dqhydr |  | 0 | K
Room automatisation |  | Dqroomaut |  | 0 | K
internal temperature |  | qint;inc | qint;inc = qint;ini + Dqstr +Dqctr +Dqemb +Dqrad +Dqim +Dqhydr +Dqroomout | 21.3 | °C
temperatur variation based on all losses |  | Dqint;inc | Dqint;inc = Dqstr +Dqctr +Dqemb +Dqrad +Dqim +Dqhydr +Dqroomout | 1.3 | K
additional loss |  | Qem;ls | Qem;ls=Qem;out *(Dqint,inc/(qint;inc-qe,comb)) | 13 | kWh
annual expenditure for the heat emission |  | eem;ls;a | eem;ls;a=(Qem;out + QemLs)/Qem;out | 1.13 | -
Auxillary energy calculation
auxiliary energy of the control system (in the period) |  | Wctr | Wctr=Pctr*tci/1000 | 0 | kWh
auxiliary energy of fans (in the period) |  | Wfan | Wfan=Pfan*th,rL*nfan/1000 | 0 | kWh
auxiliary energy |  | Wem,ls,aux | Wem,ls,aux = Wctr + Wfan | 0 | kWh
auxiliary energy (h > 4 m) - systems with direct heating |  | Wem,ls,aux | Wem;ls;aux=PH;aux*th/1000 | 0 | kWh

## Output
Output Data EN 15316-2
auxiliary energy – heat emission | Wem;ls,aux | 0 | kWh
additional heat losses of heat emission | Qem;ls | 13 | kWh
room temperature | qint, inc | 21.3 | °C
annual expenditure for the heat emission | eem, ls,a | 1.13 | -