## Tabelle1 (hidden)
Room | 1 | 2 | 1 | 2
BE | 1 | 1 | 2 | 2 | 2
θ_int,i | 18 | 20 | 20 | 18 | unheated (winter garden, glazed balkony, etc.) | °C
n_min | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1/h
| BE1 ¦ Room1 | BE1 ¦ Room2 | BE2 ¦ Room1 | BE2 ¦ Room2 | BE2 ¦ unheated
| θ_int,i: 18 °C | θ_int,i: 20 °C | θ_int,i: 20 °C | θ_int,i: 18 °C | θ_int,i: unheated (winter garden, glazed balkony, etc.) °C
| n_min: 0,5 1/h | n_min: 0,5 1/h | n_min: 0,5 1/h | n_min: 0,5 1/h | n_min: 0,5 1/h
| BE1 ¦ Room1 θ_int,i: 18 °C n_min: 0,5 1/h | BE1 ¦ Room2 θ_int,i: 20 °C n_min: 0,5 1/h | BE2 ¦ Room1 θ_int,i: 20 °C n_min: 0,5 1/h | BE2 ¦ Room2 θ_int,i: 18 °C n_min: 0,5 1/h | BE2 ¦ unheated θ_int,i: unheated (winter garden, glazed balkony, etc.) °C n_min: 0,5 1/h
Shared hallway (unheated)
5,0
2,0
6,0
1,5
3,5
4,0
1,5 x 1,6
1,5 x 1,6
1,5 x 1,6
3,8 x 2,1
1,5 x 2,1
Apartment 1, regularly occupied
Apartment 2, regularly occupied
N
1,5 x 1,6
BE2 | Room1 θ_int,i: 20 °C n_min: 0,5 1/h
BE1 | Room1 θ_int,i: 18 °C n_min: 0,5 1/h
BE1 | Room2 θ_int,i: 20 °C n_min: 0,5 1/h
BE2 | Room2 θ_int,i: 18 °C n_min: 0,5 1/h
BE2 | unheated θ_int,i: unheated (winter garden, glazed balkony, etc.) °C n_min: 0,5 1/h
Storey height: 2,8
Internal height: 2,6
Wall thickness: 0,3

## INFO
DISCLAIMER:
· This spreadsheet has been developed in the framework of the preparation and revision of the set of EN or ISO standards on the energy performance of buildings, to support the European "Energy Performance of Buildings Directive" recast (EPBD-recast, directive 2010/31/EU).
· It is meant for use by CEN and ISO technical committee(s) and the working group(s) working on the preparation or revision of the EPB-standard to which this spreadsheet applies. The spreadsheet supports checking that all equations in the developed standard are consistent and can be linked with other relevant standards. It is not meant to perform a full or partial energy performance calculation.
· The spreadsheet supports the expert user of the standards, in particular those who want to review the content of the standard and those who want to translate the standard to a software, to understand the correct interpretation of the equations and calculation steps in the standard.
· Although it has been developed with care, neither the technical committee(s), nor the working group(s) and experts related to the EPB- standard to which this spreadsheet applies warrant that the calculations and procedures in this spreadsheet are free of errors. The technical committees as well as the working groups and their respective members expressly disclaim any liability or responsibility arising from use of this spreadsheet, or any consequences thereof. Any responsibility arising from the use of this spreadsheet lies with the user.
DRAFT VERSION:
· As long as the associated EPB standard or any of the other EPB standards to which it is directly linked are in a draft stage, this spreadsheet is also a draft version only.
WARNINGS:
· Note that the spreadsheet may not allow testing all calculation options that are possible according to the standard to which it applies. This remark applies in particular but not only to limitations on the number instances of a variable that can be considered.
· In case of differences, the standard should be regarded as the reference, not the spreadsheet. However, during the standard's drafting phase, shortcomings in the draft standard may have been detected and dealt with in the spreadsheets (ideally, such differences are marked).
· Note also that these spreadsheets are purely intended for testing and demonstration and therefore not aiming to be user friendly or to be protected against wrong or improper use.
TERMS OF USE:
· The user is not allowed to redistribute a modified version of this spreadsheet.
· The author(s) would appreciate your feed back on the spreadsheet via the comment sheets for the associated draft standard to be prepared by the national standards bodies during enquiry of the draft standard(s),

## Calculation, Results
Transmission
Building entity | Heated space | Internal design temperature | Building element | Adjacent space | Index | Area | Thermal transmittance | Thermal bridges | Temperature of adjacent space | Exposed periphery (floors) | Depth below ground level (floors, basement walls) | Geometric parameter floor slab | Influence of ground water and annual temperature variation | Equivalent U-value (floors, basement walls) | Temperature adjustment factor | Heat transfer coefficient from BE directly or indirectly to exterior |  | - | Heat transfer coefficient between adjoining rooms and BE |  | - |  | Internal temperature of BE (looked upon as unheated BE) | Transmission heat loss coefficient from i to x | Transmission heat loss | Design transmission heat loss
BE/z | i | θ_int,i | k | - | - | A_k | U_k | ΔU_TB | θ_a | P | z | B' | f_GW,k * f_θann | U_equiv,k | f_ix | H_ue |  | H_ue * θ_e | H_ju |  | H_ju * θ_j |  | θ_u | H_T,ix | Φ_T,ix | Φ_T,i | Φ_T,z | Φ_T,build
- | - | °C | - | - | - | m² | W/m²K | W/m²K | °C | m | m | m | - | W/m²K | - | W/K |  |  | W/K |  | W |  | °C | W/K | W | W | W | W
BE1 | BE1 ¦ Room1 | 18 | Floor | Ground | ig | 28 | 0.7 | 0.05 | 10 | 11 | 0 | 5.0909 | 1.45 | 0.32171 | 0.26667 | 4.0244 | 64.1899 | -770.2792 | - | 8.4 | - | 168 | 10 | 4.0244 | 120.7322 | 863.3322 | 2065.8691 | 3380.4899
BE1 | BE1 ¦ Room1 | 18 | Ceiling | Unheated space | iae | 28 | 0.4 | 0.05 | - | - | - | - | - | - | 0.7 | 8.82 |  |  | - |  | - |  |  | 8.82 | 264.6
BE1 | BE1 ¦ Room1 | 18 | Ext Wall N | Exterior | ie | 19.6 | 0.3 | 0.05 | -12 | - | - | - | - | - | 1 | 6.86 |  |  | - |  | - |  |  | 6.86 | 205.8 |  |  |  | acb | 123 | Input / project specifications
BE1 | BE1 ¦ Room1 | 18 | Int Wall S 1 | BE1 ¦ Room2 | ia | 14 | 1.2 | 0.05 | 20 | - | - | - | - | - | -0.066667 | - |  |  | - |  | - |  |  | -1.1667 | -35 |  |  |  | acb | 124 | Repeated occurrence of input data
BE1 | BE1 ¦ Room1 | 18 | Int Wall S 2 | Unheated space | iae | 5.6 | 0.7 | 0.05 | - | - | - | - | - | - | 0.4 | 1.68 |  |  | - |  | - |  |  | 1.68 | 50.4 |  |  |  | acb | 125 | Calculated data: interim/end results
BE1 | BE1 ¦ Room1 | 18 | Int Wall E | BE2 ¦ Room1 | iaBE | 11.2 | 0.7 | 0.05 | 10 | - | - | - | - | - | 0.26667 | - |  |  | 8.4 |  | 168 |  |  | 2.24 | 67.2 |  |  |  | acb | 126
BE1 | BE1 ¦ Room1 | 18 | Ext Wall W | Exterior | ie | 8.8 | 0.3 | 0.05 | -12 | - | - | - | - | - | 1 | 3.08 |  |  | - |  | - |  |  | 3.08 | 92.4 |  |  |  | acb | 127
BE1 | BE1 ¦ Room1 | 18 | Ext Window W | Exterior | ie | 2.4 | 1.3 | 0.05 | -12 | - | - | - | - | - | 1 | 3.24 |  |  | - |  | - |  |  | 3.24 | 97.2 |  |  |  | acb | 125 | Repeated occurrence of calculated data
BE1 | BE1 ¦ Room2 | 20 | Floor | Ground | ig | 25 | 0.7 | 0.05 | 10 | 10 | 0 | 5 | 1.45 | 0.32345 | 0.3125 | 4.2305 |  |  | - |  | - |  |  | 4.2305 | 135.3769 | 1202.5369 |  |  | acb | 126
BE1 | BE1 ¦ Room2 | 20 | Ceiling | Unheated space | iae | 25 | 0.4 | 0.05 | - | - | - | - | - | - | 0.7 | 7.875 |  |  | - |  | - |  |  | 7.875 | 252 |  |  |  | acb | 127
BE1 | BE1 ¦ Room2 | 20 | Int Wall N | BE1 ¦ Room1 | ia | 14 | 1.2 | 0.05 | 18 | - | - | - | - | - | 0.0625 | - |  |  | - |  | - |  |  | 1.0938 | 35
BE1 | BE1 ¦ Room2 | 20 | Ext Wall S | Exterior | ie | 6.02 | 0.3 | 0.05 | -12 | - | - | - | - | - | 1 | 2.107 |  |  | - |  | - |  |  | 2.107 | 67.424
BE1 | BE1 ¦ Room2 | 20 | Ext Window S | Exterior | ie | 7.98 | 1.3 | 0.05 | -12 | - | - | - | - | - | 1 | 10.773 |  |  | - |  | - |  |  | 10.773 | 344.736
BE1 | BE1 ¦ Room2 | 20 | Int Wall E | Unheated space | iae | 14 | 0.7 | 0.05 | - | - | - | - | - | - | 0.4 | 4.2 |  |  | - |  | - |  |  | 4.2 | 134.4
BE1 | BE1 ¦ Room2 | 20 | Ext Wall W | Exterior | ie | 11.6 | 0.3 | 0.05 | -12 | - | - | - | - | - | 1 | 4.06 |  |  | - |  | - |  |  | 4.06 | 129.92
BE1 | BE1 ¦ Room2 | 20 | Ext Window W | Exterior | ie | 2.4 | 1.3 | 0.05 | -12 | - | - | - | - | - | 1 | 3.24 |  |  | - |  | - |  |  | 3.24 | 103.68
BE2 | BE2 ¦ Room1 | 20 | Floor | Ground | ig | 24 | 0.7 | 0.05 | 10 | 10 | 0 | 4.8 | 1.45 | 0.32736 | 0.3125 | 4.1038 | 44.5351 | -534.4213 | - | 8.4 | - | 151.2 | 10 | 4.1038 | 131.322 | 851.282 | 1465.8208
BE2 | BE2 ¦ Room1 | 20 | Ceiling | Unheated space | iae | 24 | 0.4 | 0.05 | - | - | - | - | - | - | 0.7 | 7.56 |  |  | - |  | - |  |  | 7.56 | 241.92
BE2 | BE2 ¦ Room1 | 20 | Ext Wall N | Exterior | ie | 14 | 0.3 | 0.05 | -12 | - | - | - | - | - | 1 | 4.9 |  |  | - |  | - |  |  | 4.9 | 156.8
BE2 | BE2 ¦ Room1 | 20 | Int Wall S | BE2 ¦ Room2 | ia | 14 | 1.2 | 0.05 | 18 | - | - | - | - | - | 0.0625 | - |  |  | - |  | - |  |  | 1.0938 | 35
BE2 | BE2 ¦ Room1 | 20 | Ext Wall E | Exterior | ie | 8.8 | 0.3 | 0.05 | -12 | - | - | - | - | - | 1 | 3.08 |  |  | - |  | - |  |  | 3.08 | 98.56
BE2 | BE2 ¦ Room1 | 20 | Ext Window E | Exterior | ie | 2.4 | 1.3 | 0.05 | -12 | - | - | - | - | - | 1 | 3.24 |  |  | - |  | - |  |  | 3.24 | 103.68
BE2 | BE2 ¦ Room1 | 20 | Int Wall W | BE1 ¦ Room1 | iaBE | 11.2 | 0.7 | 0.05 | 10 | - | - | - | - | - | 0.3125 | - |  |  | 8.4 |  | 151.2 |  |  | 2.625 | 84
BE2 | BE2 ¦ Room2 | 18 | Floor | Ground | ig | 21 | 0.7 | 0.05 | 10 | 3.5 | 0 | 12 | 1.45 | 0.23255 | 0.26667 | 2.2943 |  |  | - |  | - |  |  | 2.2943 | 68.8288 | 607.5388
BE2 | BE2 ¦ Room2 | 18 | Ceiling | Unheated space | iae | 21 | 0.4 | 0.05 | - | - | - | - | - | - | 0.7 | 6.615 |  |  | - |  | - |  |  | 6.615 | 198.45
BE2 | BE2 ¦ Room2 | 18 | Int Wall N | BE2 ¦ Room 1 | ia | 16.8 | 1.2 | 0.05 | 20 | - | - | - | - | - | -0.066667 | - |  |  | - |  | - |  |  | -1.4 | -42
BE2 | BE2 ¦ Room2 | 18 | Int Wall S | Unheated space | iae | 11.25 | 0.7 | 0.05 | - | - | - | - | - | - | 0.4 | 3.375 |  |  | - |  | - |  |  | 3.375 | 101.25
BE2 | BE2 ¦ Room2 | 18 | Int Window S 1 | Unheated space | iae | 3.15 | 1.3 | 0.05 | - | - | - | - | - | - | 0.4 | 1.701 |  |  | - |  | - |  |  | 1.701 | 51.03
BE2 | BE2 ¦ Room2 | 18 | Int Window S 2 | Unheated space | iae | 2.4 | 1.3 | 0.05 | - | - | - | - | - | - | 0.4 | 1.296 |  |  | - |  | - |  |  | 1.296 | 38.88
BE2 | BE2 ¦ Room2 | 18 | Ext Wall E | Exterior | ie | 9.8 | 0.3 | 0.05 | -12 | - | - | - | - | - | 1 | 3.43 |  |  | - |  | - |  |  | 3.43 | 102.9
BE2 | BE2 ¦ Room2 | 18 | Int Wall W | Unheated space | iae | 9.8 | 0.7 | 0.05 | - | - | - | - | - | - | 0.4 | 2.94 |  |  | - |  | - |  |  | 2.94 | 88.2
Ventilation | [10 empty] | Total
Ventilation zone | Ventilation type | Heated space | Internal design temperature | Minimum air flow rate of the heated space i | Internal volume of i | Minimum air flow of i | Design ventilation heat loss |  |  |  | Ventilation zone | Heated space | Design heat load
z | - | i | θ_int,i | n_min,i | V_i | q_v,min,i | Φ_v,i | Φ_v,z | Φ_v,build |  | z | i | Φ_HL,i | Φ_HL,BE | Φ_HL,build
- | - | - | °C | 1/h | m³ | m³/h | W | W | W |  | - | - | W
BE1 | Natural ventilation, air-tight building | BE1 ¦ Room1 | 18 | 0.5 | 60.4565 | 30.2282 | 308.3282 | 300.5722 | 552.1376 |  | BE1 | BE1 ¦ Room1 | 1171.6604 | 2366.4413 | 3932.6275
|  | BE1 ¦ Room2 | 20 | 0.5 | 53.8265 | 26.9132 | 292.8162 |  |  |  |  | BE1 ¦ Room2 | 1495.353
BE2 | Natural ventilation, air-tight building | BE2 ¦ Room1 | 20 | 0.5 | 51.2265 | 25.6132 | 278.6722 | 251.5654 |  |  | BE2 | BE2 ¦ Room1 | 1129.9542 | 1717.3862
|  | BE2 ¦ Room2 | 18 | 0.5 | 44.0115 | 22.0057 | 224.4587 |  |  |  |  | BE2 ¦ Room2 | 831.9975
Note on J3: Jens Rosenkranz: Default value from national or informative annex
Note on O6: Jens Rosenkranz: Default value from national or informative annex
Note on P6: Jens Rosenkranz: U_equiv,k = a/(b + (c1 + B')^n1 + (c2 + z)^n2 + U_k^n3)
Note on Q6: Jens Rosenkranz: Calculated with general formula for temperature adjustment factor: f_ix = (θ*_int,i - θ_x)/(θ_int,i - θ_e)
Note on Q7: Jens Rosenkranz: Default value from national or informative annex
Note on Q8: Jens Rosenkranz: no adjustment required, but general formula for temperature adjustment factor can still be applied: f_ix = (θ*_int,i - θ_x)/(θ_int,i - θ_e)
Note on Q9: Jens Rosenkranz: Calculated with general formula for temperature adjustment factor: f_ix = (θ*_int,i - θ_x)/(θ_int,i - θ_e)
Note on Q10: Jens Rosenkranz: Default value from national or informative annex
Note on Q11: Jens Rosenkranz: Calculated with general formula for temperature adjustment factor: f_ix = (θ*_int,i - θ_x)/(θ_int,i - θ_e)
Note on Q12: Jens Rosenkranz: no adjustment required, but general formula for temperature adjustment factor can still be applied: f_ix = (θ*_int,i - θ_x)/(θ_int,i - θ_e)
Note on Q13: Jens Rosenkranz: no adjustment required, but general formula for temperature adjustment factor can still be applied: f_ix = (θ*_int,i - θ_x)/(θ_int,i - θ_e)
Note on O14: Jens Rosenkranz: Default value from national or informative annex
Note on P14: Jens Rosenkranz: U_equiv,k = a/(b + (c1 + B')^n1 + (c2 + z)^n2 + U_k^n3)
Note on Q14: Jens Rosenkranz: Calculated with general formula for temperature adjustment factor: f_ix = (θ*_int,i - θ_x)/(θ_int,i - θ_e)
Note on Q15: Jens Rosenkranz: Default value from national or informative annex
Note on Q16: Jens Rosenkranz: Calculated with general formula for temperature adjustment factor: f_ix = (θ*_int,i - θ_x)/(θ_int,i - θ_e)
Note on Q17: Jens Rosenkranz: no adjustment required, but general formula for temperature adjustment factor can still be applied: f_ix = (θ*_int,i - θ_x)/(θ_int,i - θ_e)
Note on Q18: Jens Rosenkranz: no adjustment required, but general formula for temperature adjustment factor can still be applied: f_ix = (θ*_int,i - θ_x)/(θ_int,i - θ_e)
Note on Q19: Jens Rosenkranz: Default value from national or informative annex
Note on Q20: Jens Rosenkranz: no adjustment required, but general formula for temperature adjustment factor can still be applied: f_ix = (θ*_int,i - θ_x)/(θ_int,i - θ_e)
Note on Q21: Jens Rosenkranz: no adjustment required, but general formula for temperature adjustment factor can still be applied: f_ix = (θ*_int,i - θ_x)/(θ_int,i - θ_e)
Note on O22: Jens Rosenkranz: Default value from national or informative annex
Note on P22: Jens Rosenkranz: U_equiv,k = a/(b + (c1 + B')^n1 + (c2 + z)^n2 + U_k^n3)
Note on Q22: Jens Rosenkranz: Calculated with general formula for temperature adjustment factor: f_ix = (θ*_int,i - θ_x)/(θ_int,i - θ_e)
Note on Q23: Jens Rosenkranz: Default value from national or informative annex
Note on Q24: Jens Rosenkranz: no adjustment required, but general formula for temperature adjustment factor can still be applied: f_ix = (θ*_int,i - θ_x)/(θ_int,i - θ_e)
Note on Q25: Jens Rosenkranz: Calculated with general formula for temperature adjustment factor: f_ix = (θ*_int,i - θ_x)/(θ_int,i - θ_e)
Note on Q26: Jens Rosenkranz: no adjustment required, but general formula for temperature adjustment factor can still be applied: f_ix = (θ*_int,i - θ_x)/(θ_int,i - θ_e)
Note on Q27: Jens Rosenkranz: no adjustment required, but general formula for temperature adjustment factor can still be applied: f_ix = (θ*_int,i - θ_x)/(θ_int,i - θ_e)
Note on Q28: Jens Rosenkranz: Calculated with general formula for temperature adjustment factor: f_ix = (θ*_int,i - θ_x)/(θ_int,i - θ_e)
Note on O29: Jens Rosenkranz: Default value from national or informative annex
Note on P29: Jens Rosenkranz: U_equiv,k = a/(b + (c1 + B')^n1 + (c2 + z)^n2 + U_k^n3)
Note on Q29: Jens Rosenkranz: Calculated with general formula for temperature adjustment factor: f_ix = (θ*_int,i - θ_x)/(θ_int,i - θ_e)
Note on Q30: Jens Rosenkranz: Default value from national or informative annex
Note on Q31: Jens Rosenkranz: Calculated with general formula for temperature adjustment factor: f_ix = (θ*_int,i - θ_x)/(θ_int,i - θ_e)
Note on Q32: Jens Rosenkranz: Default value from national or informative annex
Note on Q33: Jens Rosenkranz: Default value from national or informative annex
Note on Q34: Jens Rosenkranz: Default value from national or informative annex
Note on Q35: Jens Rosenkranz: no adjustment required, but general formula for temperature adjustment factor can still be applied: f_ix = (θ*_int,i - θ_x)/(θ_int,i - θ_e)
Note on Q36: Jens Rosenkranz: Default value from national or informative annex

## Input data
Building entity / Ventilation zone | Ventilation type | Heated space | Internal design temperature | Minimum air flow rate of the heated space i | Annual mean external temperature | External design temperature | Depth of water table below floor slab | Minimum temperature of unoccupied spaces / building entities | Temperature- and volume-specific thermal capacity of air | Additional heating-up capacities | Thermal transmittance
BE/z | - | i | θ_int,i | n_min,i | [6 empty] | External walls | Internal walls between rooms of one BE | Internal walls between BEs, floors | Ceiling | Windows | Thermal bridges
- | - | - | °C | 1/h | θ_me | θ_e | z | θ_x,min | ρ * c_w | - | U |  |  |  |  | ΔU_TB
BE1 | Natural ventilation, air-tight building | BE1 ¦ Room1 | 18 | 0.5 | °C | °C | m | °C | Wh/m³K | - | W/m²K
|  | BE1 ¦ Room2 | 20 | 0.5 | 10 | -12 | > 1 | 10 | 0.34 | none | 0.3 | 1.2 | 0.7 | 0.4 | 1.3 | 0.05
BE2 | Natural ventilation, air-tight building | BE2 ¦ Room1 | 20 | 0.5
|  | BE2 ¦ Room2 | 18 | 0.5
Note on H5: Jens Rosenkranz: Further distinction possible (reference sites etc.)