## INFO
This spreadsheet:
This spreadsheet is part of a series, to support the implementation and use of the set of (CEN, ISO) EPB standards
(see below)
Main related standard(s): | ISO 52016-1:2017, Energy performance of buildings — Energy needs for heating and cooling, internal temperatures and sensible and latent heat loads — Part 1: Calculation procedures
Demo input data file
Spreadsheet created by: | Dick van Dijk (EPB Center expert)
Contact: | https://epb.center/contact/
Date: | 2019-11-20
Replaces file: None Date: not applicable
Detailed info: | See sheet "Explanation"
The series of spreadsheets to support the implementation and use of the set of EPB standards:
EPB spreadsheets: | This spreadsheet is part of a series of spreadsheets to support the implementation and use of the set of (CEN, ISO) EPB standards
Each of these spreadsheets complies with a specific template and follows specific rules
Main purpose: | The main purpose of these EPB spreadsheets is to support the implementation and use of the standards.
They aim to demonstrate the validity of the calculation procedures and the required input and provided output data defined in the standard.
They support the expert user of the standards, in particular those who want to review the content of the standard and those who want to translate the standard into software, to understand the correct interpretation of the formulae and calculation steps in the standard, or e.g. to explore the sensitivity for variations in input values.
Some spreadsheets have been further developed to include more advanced features or to become more user friendly (see sheet "Explanation")
Limitations: | In general, these spreadsheets do not cover the full range of calculation options that are possible according to the standard to which it applies. This concerns e.g. the number of instances of a variable, the number of time intervals and/or special calculation cases.
These spreadsheets cover only a single or a cluster of EPB standards and are not meant to perform a full energy performance calculation.
Note also that these spreadsheets are mainly intended for testing and demonstration and therefore not aiming to be user friendly or to be protected against wrong or improper use.
The spreadsheets related to the EPB standards are provided to demonstrate specific elements of the calculation procedures in the relevant standard(s). Consequently, they do not replace the EPB standards, but they shall be used along with the EPB standards.
Responsible: | In general, the preparation of the spreadsheet is a collective process in which several experts (including main developers of the standard) are involved
See "Background" below for information on the first versions of (most of) these spreadsheets
Acknowledgement: | The EPB spreadsheets produced or upgraded after 2018 have been prepared under a contract with the European Union, represented by the European Commission (Service contract ENER/C3/2017-437/SI2-785.185). Start: 21 September 2018 for 3 years. See "Background" for information on previous (2012-2017) versions of many of these spreadsheets
Disclaimer: | Although these spreadsheets have been developed with care, neither the authors or contributors warrant that the calculations and procedures in this spreadsheet are free of errors. The EPB Center expressly disclaims any liability or responsibility arising from use of this spreadsheet, or any consequences thereof. Any responsibility arising from the use of this spreadsheet lies with the user.
The information and views set out in this document are those of the author(s) and do not necessarily reflect the official opinion of the European Union. Neither the European Union institutions and bodies nor any person acting on their behalf may be held responsible for the use which may be made of the information contained therein.
Terms of use: | The user is not allowed to redistribute a modified version of this spreadsheet.
The author(s) would appreciate your feed back on the spreadsheet (see Contact above)
More information: | www.epb.center
Background: | First published versions of these spreadsheets were developed during 2012-2017, in the framework of the preparation and revision of the set of EN or ISO standards on the energy performance of buildings, to support the European "Energy Performance of Buildings Directive" recast 2010, under Mandate M/480 of the European Commission to CEN.
These first versions were meant for use by CEN and ISO Technical Committee(s) and the Working Group(s) working on the preparation or revision of the EPB-standard to which this spreadsheet applies.
These first public versions of the spreadsheets were mainly intended to support checking that all formulae in the standard under development were consistent and could be linked with other relevant (EPB) standards.
Many of these spreadsheets have been developed parallel to the preparation of the set of EPB standards under the M/480 mandate from the European Commission (2012 - 2017) and do not necessarily reflect the final status of the standard.
More information:
https://epb.center/epb-standards/background/

## Explanation
EPB standard: | (EN) ISO 52016-1:2017 | Energy performance of buildings — Energy needs for heating and cooling, internal temperatures and sensible and latent heat loads — Part 1: Calculation procedures
FILE WITH INPUT DATA THAT CAN BE COPIED TO THE CALCULATION SPREADSHEET
Responsible in ISO and/or CEN: |  | ISO/TC 163/SC 2/WG 15 in collaboration with CEN/TC 89
Convention: | Font colors and/or cell shading on calculation sheet(s):
| red font | input
| blue font | calculated
| green font | fixed
| black font | set up, various
| yellow cell | calculated with deviating formula
Run: | To copy the data from this file into the calculation spreadsheet: see Calculation spreadsheet, sheet: Method_input
Status: | Published
Main features: | This is a separate file with all input data that are needed for a calculation case, except the climatic data
In the calculation spreadsheet (sheet: Method_input) the name of this file can be filled in
and a macro can be started that copies all input data from this file into the calculation file
The calculation file can also be used directly, without separate input file,
but using the separate input files enables an easy change of cases and exchange of cases between users
To avoid incompatibility issues, the macro starts with checking whether the same version of input file and calculation file is used.
Time intervals and period: | See calculation file
Main limitations: | Not applicable for this file with Input data
Beta test version:
- The format of some cells (e.g. size, number of decimals) may need to be improved
Protection: | This file is protected against editing except for the cells where input is expected
The main reason is to prevent uncontrolled use and to keep technical support managable
More information:
CEN ISO/TR 52016-2, Energy performance of buildings
— Energy needs for heating and cooling, internal temperatures and sensible and latent heat loads
— Part 2: Explanation and justification of ISO 52016-1 and ISO 52017-1
Published June 2017
Links: | https://epb.center/documents/iso-52016-1/
includes also links to published articles and more
https://epb.center/documents/isotr-52016-2/
Overview of the meaning of each sheet in this file
Sheet |  | Description | Tab colour coding used to facilitate navigation:
INFO |  | Common info for all EPB spreadsheets, including DISCLAIMER | Red tab colour (do not touch) for INFO, Explanation and History
Explanation |  | Explanation on this spreadsheet on ISO 52016-1 / INPUT DATA
Method_input |  | Tabulated overview of all input data, according to common template for all EPB spreadsheets | Green tab colour for Method_input/calculation/output
Input_GrFl |  | Extra, integrated: Tabulated overview of all input data for ISO 13370 (ground floor th transmission), according to common template for all EPB spreadsheets | Yellow tab colour for extra sheets with I/O data or calculations
Input_0 |  | Input to control the calculation parameters, to fill the data for the building elements; plus processing to prepare the equations
Input_p |  | Input to fill the 24/7 conditions of use; plus processing to prepare the equations
History of this spreadsheet
Date | Developer | Description
2019.11.20 | Dick van Dijk | First version of separate input data file

## Method_input
XLS on ISO 52016-1 version | 2 | (to enable a check on compatibility of input data sets)
First timestep (optionally incl. initializ. 31 days) for hourly calculation |  |  | 1
Last timestep for hourly calculation |  |  | 9504
Name | Symbol | Unit | value | Validity intervala | Originb | Varyingc | Calculation method (in this input file: as much as possible combined) | Symbol in origin (if different) | Notes | Notes on the specific input (optional)
General data on the assessed object and application (ISO 52016-1:2017, Table 11) |  |  | Only column D and column K are for input
Space category for each space or group of spaces (if different from building category) | SPACECAT_TYPE | n/a | Shoebox test cases |  | ISO 52000-1 | NO |  |  | From spreadsheet version 2: no longer used; give pattern in Input_p | test note first input
Calculation case | CASE_IDENTIFIER | n/a | BESTEST 900 (variations: 640, 900, 940, 600FF, 900FF) |  | ISO 52000-1 | NO
Description | - | - | Heavyweight, continuous operation | Free text
Geometrical data list (ISO 52016-1:2017, Table 12)
Useful floor area of the thermal zone | Ause;zt | m2 | 48
Air volume of the thermal zone | Vint;a;zt | m3 | 129.6
Thermal zone related input data list (ISO 52016-1:2017, Table 13)
Areal thermal capacity of air and furniture per thermally conditioned zone (Hourly method!) | Cint;zi/Ause;zi | J/(m2·K) | 10000 | 0 to ∞ | Local or default (Table A.17) | No |  | -
Class of the internal heat capacity per thermally conditioned zone (Monthly method!) | - | - | 4 | Identifier | Local | No |  |  | ! Use number 1-> 5 for class very Light to Very heavy
INFO: this class number corresponds to the class description: | Heavy
Building element related input data list (ISO 52016-1:2017, Table 14)
Overall heat transfer coefficient for the thermal bridges, per thermal zone (excl. ground floor which is covered in sheet "Input_GrFl") | Htr;tb;zt <excl. grfl> | W/K | 0 | 0 to ∞ | M2-5.1 | Yes |  | Htb
Input data related to conditions of use and technical building systems (ISO 52016-1:2017, Table 16)
Hourly and monthly calculation procedures:
High level set-point temperature for heating in conditioned space |  | °C | 20
Moderate level set-point temperature for heating in conditioned space (not usable for monthly method) |  | °C | 10
Low level set-point temperature for heating in conditioned space ("temp.set back") |  | °C | 10 | [5 empty] | In case of switch off use low value, e.g.: -999
High level set-point temperature for cooling in conditioned space |  | °C | 27
Moderate level set-point temperature for cooling in conditioned space (not usable for monthly method) |  |  | 999
Low level set-point temperature for cooling in conditioned space (no effect in monthly method) |  | °C | 999
Hourly calculation procedures:
Available heating power, per thermally conditioned zone, per hour | ΦH;avail;ztc;t | W | 1000000 | 0 to ∞ | M3-1 | Yes | H
Available cooling power, per thermally conditioned zone, per hour | ΦC;avail;ztc;t | W | 1000000 | 0 to ∞ | M4-1 | Yes | H | QC;out;zt,j
Convective fraction of the heating system per thermally conditioned zone (if system specific) (not usable for monthly method) | fH,c ztc | - | 1 | 0 to 1 | (M3-5 or M3 system description) or default (Table A.11) | No | H |  |  | Specific for BESTEST....
Convective fraction of the cooling system per thermally conditioned zone (if system specific) (not usable for monthly method) | fC,c ztc | - | 1 | 0 to 1 | (M4-5 or M4 system description) or default (Table A.11) | No | H |  |  | Specific for BESTEST....
Set-point relative humidity for humidification, per thermally conditioned zone, per hour | φint;set;HU;ztc;t | % | 40 | 0 to 100 | M1-6 | Yes | H
Set-point relative humidity for dehumidification, per thermally conditioned zone, per hour | φint;set;DHU;ztc;t | % | 75 | 0 to 100 | M1-6 | Yes | H
Hourly and monthly calculation procedures:
Constant ventilation flow during all hrs | φV;24x7 | m3/(h.m2) | 1.107
Extra ventilation flow during moderate comfort hrs | φV;comf1 | m3/(h.m2) | 0
Extra ventilation flow during high comfort hrs | φV;comf2 | m3/(h.m2) | 0
Hourly calculation procedures:
Extra ventilation flow for cooling | φV;cool | m3/(h.m2) | See VCS_special | [5 empty] | During moderate and high occupancy, no sophisticated control as for special ventilative cooling systems
Monthly calculation procedures:
Occupancy pattern (see Notes) | [8 empty] | These data could in theory be derived from the hourly pattern for hourly calculations. However, it is not just a simple counting of hours per day occupated vs non-occupated: if these hours are divided over different parts of the day, the number of periods per day and length per intermittency is different
The duration of the period with reduced heating set-point (y=night ) | ΔtH;red;y;ztc | h | 8 | 1 to 10 | M1-6 | No | M |  | ATTENTION: temperature can drop to low ('economy') temperature set point. set n to zero, not Δt!! Example input: resid: 7; office: 13
The number of repetitions in a week of reduction period (y=night) | nrep;H;red;y;ztc | - | 0 | 0 to 7 | M1-6 | No | M |  | Example input: resid: 7; office: 5
The duration of the period with reduced heating set-point (y=day) | ΔtH;red;y;ztc | h | 10 | 1 to 12 | M1-6 | No | M |  | Example input: resid: 11; office: 8
The number of repetitions in a week of reduction period (y=day) | nrep;H;red;y;ztc | - | 0 | 0 to 7 | M1-6 | No | M |  | Example input: resid:5; office:0
The duration of the period with reduced heating set-point (y=weekend) | ΔtH;red;y;ztc | h | 48 | 1 to 48 | M1-6 | No | M |  | Example input: resid: 48; office: 48
The number of repetitions in a week of reduction period (y=weekend) | nrep;H;red;y;ztc | - | 0 | 0 to 7 | M1-6 | No | M |  | Example input: resid:0; office:1
The number of hours during the weekend with reduced temperature set-point for cooling or interruption | ΔtC;red;wknd;ztc | - | 48 | 0 to 48 | M1-6 | No | M |  | set n to zero, not Δt!! Example input: resid: 48; office: 48
The number of repetitions in a week of this intermittency | nrep;C;red;wknd;ztc | - | 0 | 0 to 7 | M1-6 | No | M |  | Residential: 0; office: 1
Extra ventilation flow during cooling & occupancy hrs | φV;cool | m3/(h.m2) | 0 |  |  |  | M |  | During moderate and high occupancy
The fraction of sensible energy need to be added for dehumidification, per type of cooling system | fDHU;C;ss | - | 0.2 | 0 to 1 | M7-5 | No | M
Internal heat gains including recoverable heat losses and moisture production (ISO 52016-1:2017, Table 18)
Hourly and monthly calculation procedures:
Constant internal heat flow rate during all hrs | qint;tot;24x7 | W/m2 | 1.453
Extra internal heat flow rate during moderately occupied hrs | qint;tot;occ1 | W/m2 | 0
Extra internal heat flow rate during highly occupied hrs | qint;tot;occ2 | W/m2 | 0
Hourly calculation procedures:
Moisture production during all hrs | Gint;24x7/Ause | kg/(m2.s) | 1.1574e-07
Extra moisture production during moderately occupied hrs | Gint;occ1/Ause | kg/(m2.s) | 0
Extra moisture production during highly occupied hrs | Gint;occ2/Ause | kg/(m2.s) | 1.6204e-06
Input data from ISO 52016-1:2017, Annex A / Annex B
Convective fraction of the internal gains into the zone | fint;c | - | 0.4 | 0 to 1 | Table A/B.11 | NO | H
Convective fraction of the solar radiation into the zone | fsol;c | - | 0.1 | 0 to 1 | Table A/B.12 | NO | H
Average difference between external air temperature and sky temperature | Δϑsky | K | 11 | -50 to +50 | H: Table A/B.19, M: Table A/B.31 | NO
Moisture absorption (positive value) or desorption (negative value) in materials in the zone | Gabs;ztc;t | kg/s | 0 | -∞ to ∞ | Table A/B.20 | NO
Dynamics correction factor for ventilation | fve;dyn;k | - | 1 | 0 to 1 | Table A/B.28 | NO | M
Reference numerical parameter for the gain utilization factor | aH;0 | - | 1 | 0 to 1 | Table A/B.34 | NO | M
Reference time constant for the gain utilization factor | tH;0 | h | 15 | 0 to 100 | Table A/B.34 | NO | M
Reference numerical parameter for the loss utilization factor | aC;0 | - | 1 | 0 to 1 | Table A/B.35 | NO | M
Reference time constant for the loss utilization factor | tC;0 | h | 15 | 0 to 100 | Table A/B.35 | NO | M
Correlation factor for intermittent cooling | bC;red;wknd | - | 0.3 | 0 to 1 | Table A/B.37 | NO | M
Efficiency of latent heat recovery | ηHU;rvd | - | 0 | 0 to 1 | Table A/B.40 | NO | M
Annually accumulated amount of moisture to be supplied per kg dry air supply | Δx∙ta;sup | kg h/kg | 0.17 | 0 to ∞ | Table A/B.41 | NO | M
Special dynamics <not provided yet>
Ventilative cooling demo operative? | VCS | - | 0 | 0 or 1 |  |  |  |  | Used in sheet Input_t, uses special VCS sheet; if =1: set also input extra vent. for cooling in monthly calc. | test note last input
Note on E6: Laurent: Indicate the correct range for this value. This information can be used for input validation.
Note on F6: Laurent: Mandatory to indicate either "local" or the code of the originating module or standard
Note on G6: Laurent: Means if this value changes from one time-step to the other

## Input_GrFl
Only column D and column I are for input
Name | Symbol | Unit | Value | Range | Origin | Varying | Notes | Notes on the specific input (optional)
Identifiers for building geometric characteristics | [6 empty] | ISO 13770:2017, Table 3
Area of floor | A | m2 | 0.00999 | ≥0 | — | No | Input in this spreadsheet is for floor type: slab-on-ground | Groundfloor
Exposed perimeter | P | m | 0.00999 | ≥0 | — | No |  | NOT APPLICABLE for BESTEST!!
Length of linear thermal bridge k | lk | m | n.a. | ≥0 | — | No | Erratum in the standard: this not an input in the standard... This is covered by the perimeter P
Thickness of the walls of the building | dw;e | m | 0.35 | ≥0 | — | No
Height of the upper surface of the floor above external ground level | h | m | n.a. | ≥0 |  | No | Not applicable for slab-on-ground floor
Depth of basement floor below ground level | z | m | n.a. | ≥0 |  | No | Not applicable for slab-on-ground floor
Identifiers for building boundary conditions | [6 empty] | ISO 13770:2017, Table 4
Annual mean internal temperature |  | °C | 23 | -50…+50 | ISO 52016-1 | No | Typically: the average between heating and cooling set point; see also next line (amplitude)
Amplitude of internal temperature variations |  | K | 3 | -50…+50 | ISO 52016-1 | No | = Half of the difference between the expected monthly max (e.g.: cooling set point) and monthly min (e.g.: heating set point)
Annual mean external temperature |  | °C | 10 | -50…+50 | ISO 52016-1 | No | Should matcthe annual mean value of the monthly mean outdoor temperature; see also next line (amplitude)
Amplitude of external temperature variations |  | K | 7 | -50…+50 | ISO 52016-1 | No | = Half of the difference between the highest and the lowest monthly mean outdoor temperature
Identifiers for periodic heat flows | [6 empty] | According to ISO 13370:2017, Annex H
Month number in which the minimum external temperature occurs | t | - | 1 | 1 or 7 | ISO 13370 Annex C | No | tau= 1 in the northern hemisphere and tau= 7 in the southern hemisphere.
Identifiers for thermal characteristics of building fabric | [6 empty] | ISO 13770:2017, Table 5
Linear thermal transmittance associated with wall/floor junction | Ψk | W/(m.K) | 0.05 | 0…10 | ISO 14683 or ISO 10211 | No
Thermal properties of the ground | [6 empty] | ISO 13770:2017, Table 7
Heat capacity of ground per volume | ρc | J/(m3·K) | 2000000 | 1...4 106 | ISO 13370, Table 7 | No | Default value (ISO 13370, Table 7, Table B.4)
Thermal properties of building materials
Thermal resistance of the floor construction (excluding the effect of the ground) | Rf | (m2.K)/W | 5.3 | 0...10 | ISO 13370 | No | ISO 13770:2017, 6.4.2 | test note last input
Note on D4: Laurent: Actual value in this calculation step
Note on E4: Laurent: Indicate the correct range for this value. This information can be used for input validation.
Note on F4: Laurent: Mandatory to indicate either "local" or the code of the originating module or standard
Note on G4: Laurent: Means if this value changes from one time-step to the other

## Input_0
| Time independent input data per building element |  | NOTE: Several input data are given in "Method_input" sheet, but still shown here, for the simple reason that the macro | [9 empty] | On this sheet:
| See sheet Method_input for general explanation on this file with input data |  | reads values from fixed cell positions in this sheet, So in the "Method_input" sheet rows may be reorganised, | [9 empty] | Input according to ISO 52016-1:2017, 6.5.7 and 6.5.8
while this sheet remains uncorrupted
[12 empty] | Class id. | Class | Monthly method, internal capacity, Cm;int;eff;ztc /Ag | Hourly method, specific heat capacity of opaque elements, κm;op
[14 empty] | J/(m2·K) | J/(m2·K)
[12 empty] | 1 | Very light | 80000 | 50000
[12 empty] | 2 | Light | 110000 | 75000
[12 empty] | 3 | Medium | 165000 | 110000
[12 empty] | 4 | Heavy | 260000 | 175000
[8 empty] | Explanation of element types: |  |  |  | 5 | Very heavy | 370000 | 250000
[8 empty] | (Sub-)types: | Description |  |  |  |  | Table 21 | Table A/B.14
[8 empty] | OP | Opaque, External environment
[8 empty] | W | Window or door, External environment
[8 empty] | GR | Ground ->>>!ATTENTION: requires extra input in sheet input_GrFl; Af and Rf;eff to be manually copied from sheet calc_GrFl to this sheet
[8 empty] | AD | Adiabatic; (assuming symmetry): use input for half of the element!! ATTENTION: a_sol and input for IR_sky (Fsky) need to be set to zero; hce and hre are ignored
[8 empty] | NA | Not available: if this type is detected this plus all next elements are ignored
Class
[8 empty] | for OP, AD, GR: | I, E, IE, M or D: th.capacity by approximation near Internal surface, near External surface, both I and E, near Middle or evenly Distributed
| ATTENTION: for ground floor: | [6 empty] | for W: | F, V1, V2: fixed properties or variable properties read from Input_t column "V1" resp. "V2"; max two variable windows!
| Rc;eli_inp = Rf;eff (to be copied manually from sheet "Calc_GrFl", Cell D11) | [7 empty] | (default: F) | If V1 or V2: the fixed values in this sheet Input_0 will still be used for the monthly method, to calculate the monthly heat transfer and gains
Row nr per element | Data per element | Eli |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Sums or sumproducts |  |  |  | Notes on the specific input (optional)
0 | Comment | Name | Unit | ground fl - as external element | wall S | window S | wall E | wall W | wall N | flat roof | dummy | dummy | dummy | dummy | dummy | dummy | dummy | dummy | dummy | dummy | dummy | dummy | dummy |  |  |  |  | test note 1
1 | Explan. in table above | Subtype | - | OP | OP | W | OP | OP | OP | OP | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
2 |  | Class | - | I | I | F | I | I | I | D | D | D | D | D | D | D | D | D | D | D | D | D | D
3 | !!!! Per element: input either U or R!! Attention: in this spreadsheet U-value of windows is based on window area (incl.frame) | Ueli_inp | W/(m2K) |  |  | 2.984 |  |  |  |  | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8
4 | !!!! (so: keep one row empty!!) | Class: Rc;eli_inp; -: (m2K)/W; I: 25.175; I: 1.797; I: 1.797; I: 1.797; I: 1.797; D: 2.992
5 | if opq or floor (but actual calc. in this spreadsheet is more flexible: values are used for each node!) | κm;eli | J/(m2K) | 110000 | 175000 | 0 | 175000 | 175000 | 175000 | 50000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Area shall be set to zero if "NA" |  |  | In this example: actual values instead of default values per Class from Table 13
6 | Attention: in this spreadsheet, if transparent: window area (incl.frame) | Aeli | m2 | 48 | 9.6 | 12 | 16.2 | 16.2 | 21.6 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.6 | Aeli;tot | m2 | Used in macro
7 | if opq (but actual calc. in this spreadsheet is more flexible: values are used for each node!) | asol;eli | - | 0 | 0.6 | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Area shall be set to zero if "NA"
8 | if transparant Attention: in this spreadsheet g-value is based on window area (incl.frame) | gw;eli | - | 0 | 0 | 0.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Columns for chosen Or. and Tilt shall be made available in sheet ClimData! | Orientation and tilt | For example SV, S45, EV, E30, NV, WV,W135, etc. and e.g. HOR | HOR | SV | SV | EV | WV | NV | HOR | SV | SV | SV | SV | SV | SV | SV | SV | SV | SV | SV | SV | SV
10 |  | (void row) | (void row)
11 |  | hci;eli | W/(m2K) | 0.7 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 462.6 | Σ(Aeli*hci;eli) | W/(m2K), W/K | Used in macro
12 |  | hri;eli | W/(m2K) | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | hri;elk;mn=Σ(Aelk/Aeli;tot)*hri;elk | W/(m2K) | Used in macro
13 | hce and hre are ignored for ground floor (but avoid zero values) | hce;eli | W/(m2K) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | !! For gr.floor: Hce, hre are ignored, but do not enter zero's
14 |  | hre;eli | W/(m2K) | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14
15 | View factor between eli and sky | Fsk;eli | - | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
16 | For hrly calculation: solar shading by obstacle number (1) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Select number on sheet Calc_shade (in preparation)
17 | For hrly calculation: solar shading by obstacle number (2) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | For hrly calculation: solar shading by overhang number |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | For mnthly calculation: direct shading reduction factor number |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | test note
20

## Input_p
HOURLY METHOD: | Weekly schedules | Used for internal heat and moisture gains |  |  | Used for temperature control and ventilation |  |  | Not yet used! |  |  | Not yet used! |  | Notes on the specific input (optional)
Manual input per hour |  | Occupancy level 0=low, 1=moderate; 2=high; per hour |  |  | Comfort level 0=low, 1=moderate; 2=high; per hour |  |  | Operation (1) level 0=off, 1=not yet used.; 2=on |  |  | Operation (2) level 0=off, 1=not yet used.; 2=on |  | test note 00
|  | Occupancy level | Occupancy level |  | Comfort level | Comfort level |  | Operation level | Operation level |  | Operation level | Operation level
| Hr of day | Weekday (Mo-Fri) | Weekend (Sat+Sun) |  | Weekday (Mo-Fri) | Weekend (Sat+Sun) |  | Weekday (Mo-Fri) | Weekend (Sat+Sun) |  | Weekday (Mo-Fri) | Weekend (Sat+Sun)
| 1 | 2 | 2 | 1 | 2 | 2 | 1 | 2 | 2 | 1 | 2 | 2 | Case 900: continuous heating
| 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| 3 | 2 | 2 | 3 | 2 | 2 | 3 | 2 | 2 | 3 | 2 | 2
| 4 | 2 | 2 | 4 | 2 | 2 | 4 | 2 | 2 | 4 | 2 | 2
| 5 | 2 | 2 | 5 | 2 | 2 | 5 | 2 | 2 | 5 | 2 | 2
| 6 | 2 | 2 | 6 | 2 | 2 | 6 | 2 | 2 | 6 | 2 | 2
| 7 | 2 | 2 | 7 | 2 | 2 | 7 | 2 | 2 | 7 | 2 | 2
| 8 | 2 | 2 | 8 | 2 | 2 | 8 | 2 | 2 | 8 | 2 | 2
| 9 | 2 | 2 | 9 | 2 | 2 | 9 | 2 | 2 | 9 | 2 | 2
| 10 | 2 | 2 | 10 | 2 | 2 | 10 | 2 | 2 | 10 | 2 | 2
| 11 | 2 | 2 | 11 | 2 | 2 | 11 | 2 | 2 | 11 | 2 | 2
| 12 | 2 | 2 | 12 | 2 | 2 | 12 | 2 | 2 | 12 | 2 | 2
| 13 | 2 | 2 | 13 | 2 | 2 | 13 | 2 | 2 | 13 | 2 | 2
| 14 | 2 | 2 | 14 | 2 | 2 | 14 | 2 | 2 | 14 | 2 | 2
| 15 | 2 | 2 | 15 | 2 | 2 | 15 | 2 | 2 | 15 | 2 | 2
| 16 | 2 | 2 | 16 | 2 | 2 | 16 | 2 | 2 | 16 | 2 | 2
| 17 | 2 | 2 | 17 | 2 | 2 | 17 | 2 | 2 | 17 | 2 | 2
| 18 | 2 | 2 | 18 | 2 | 2 | 18 | 2 | 2 | 18 | 2 | 2
| 19 | 2 | 2 | 19 | 2 | 2 | 19 | 2 | 2 | 19 | 2 | 2
| 20 | 2 | 2 | 20 | 2 | 2 | 20 | 2 | 2 | 20 | 2 | 2
| 21 | 2 | 2 | 21 | 2 | 2 | 21 | 2 | 2 | 21 | 2 | 2
| 22 | 2 | 2 | 22 | 2 | 2 | 22 | 2 | 2 | 22 | 2 | 2
| 23 | 2 | 2 | 23 | 2 | 2 | 23 | 2 | 2 | 23 | 2 | 2
| 24 | 2 | 2 | 24 | 2 | 2 | 24 | 2 | 2 | 24 | 2 | 2 | test note24