## INFO
This spreadsheet:
This spreadsheet is part of a series, to support the implementation and use of the set of (CEN, ISO) EPB standards
(see below)
Main related standard(s): | ISO 52016-1:2017, Energy performance of buildings — Energy needs for heating and cooling, internal temperatures and sensible and latent heat loads — Part 1: Calculation procedures
Demo input data file
Spreadsheet created by: | Dick van Dijk (EPB Center expert)
Contact: | https://epb.center/contact/
Date: | 2023-09-21
Replaces file: Demo_ISO_52016-1_Input_[Case ..]_2019-11-20 Date: 2019-11-20
Detailed info: | See sheet "Explanation"
The series of spreadsheets to support the implementation and use of the set of EPB standards:
EPB spreadsheets: | This spreadsheet is part of a series of spreadsheets to support the implementation and use of the set of (CEN, ISO) EPB standards
Each of these spreadsheets complies with a specific template and follows specific rules
Main purpose: | The main purpose of these EPB spreadsheets is to support the implementation and use of the standards.
They aim to demonstrate the validity of the calculation procedures and the required input and provided output data defined in the standard.
They support the expert user of the standards, in particular those who want to review the content of the standard and those who want to translate the standard into software, to understand the correct interpretation of the formulae and calculation steps in the standard, or e.g. to explore the sensitivity for variations in input values.
Some spreadsheets have been further developed to include more advanced features or to become more user friendly (see sheet "Explanation")
Limitations: | In general, these spreadsheets do not cover the full range of calculation options that are possible according to the standard to which it applies. This concerns e.g. the number of instances of a variable, the number of time intervals and/or special calculation cases.
These spreadsheets cover only a single or a cluster of EPB standards and are not meant to perform a full energy performance calculation.
Note also that these spreadsheets are mainly intended for testing and demonstration and therefore not aiming to be user friendly or to be protected against wrong or improper use.
The spreadsheets related to the EPB standards are provided to demonstrate specific elements of the calculation procedures in the relevant standard(s). Consequently, they do not replace the EPB standards, but they shall be used along with the EPB standards.
Responsible: | In general, the preparation of the spreadsheet is a collective process in which several experts (including main developers of the standard) are involved
See "Background" below for information on the first versions of (most of) these spreadsheets
Acknowledgement: | The EPB spreadsheets produced or upgraded after 2018 have been prepared under a contract with the European Union, represented by the European Commission (Service contract ENER/C3/2017-437/SI2-785.185). Start: 21 September 2018 for 3 years. See "Background" for information on previous (2012-2017) versions of many of these spreadsheets
Disclaimer: | Although these spreadsheets have been developed with care, neither the authors or contributors warrant that the calculations and procedures in this spreadsheet are free of errors. The EPB Center expressly disclaims any liability or responsibility arising from use of this spreadsheet, or any consequences thereof. Any responsibility arising from the use of this spreadsheet lies with the user.
The information and views set out in this document are those of the author(s) and do not necessarily reflect the official opinion of the European Union. Neither the European Union institutions and bodies nor any person acting on their behalf may be held responsible for the use which may be made of the information contained therein.
Terms of use: | The user is not allowed to redistribute a modified version of this spreadsheet.
The author(s) would appreciate your feed back on the spreadsheet (see Contact above)
More information: | www.epb.center
Background: | First published versions of these spreadsheets were developed during 2012-2017, in the framework of the preparation and revision of the set of EN or ISO standards on the energy performance of buildings, to support the European "Energy Performance of Buildings Directive" recast 2010, under Mandate M/480 of the European Commission to CEN.
These first versions were meant for use by CEN and ISO Technical Committee(s) and the Working Group(s) working on the preparation or revision of the EPB-standard to which this spreadsheet applies.
These first public versions of the spreadsheets were mainly intended to support checking that all formulae in the standard under development were consistent and could be linked with other relevant (EPB) standards.
Many of these spreadsheets have been developed parallel to the preparation of the set of EPB standards under the M/480 mandate from the European Commission (2012 - 2017) and do not necessarily reflect the final status of the standard.
More information:
https://epb.center/epb-standards/background/

## Explanation
FILE WITH INPUT DATA THAT CAN BE COPIED TO THE CALCULATION SPREADSHEET
EPB standard: | (EN) ISO 52016-1:2017 | Energy performance of buildings — Energy needs for heating and cooling, internal temperatures and sensible and latent heat loads — Part 1: Calculation procedures
plus partially: | (EN) ISO 13370:2017 | Thermal performance of buildings — Heat transfer via the ground — Calculation methods
plus fully (NEW!): | (EN) ISO 52016-3:2023 | Energy performance of buildings — Energy needs for heating and cooling, internal temperatures and sensible and latent heat loads — Part 3: Calculation procedures regarding adaptive building envelope elements procedures incl. draft of Amendment:2023
Responsible in ISO and/or CEN: |  | ISO/TC 163/SC 2/WG 15 in collaboration with CEN/TC 89
Convention: | Font colors and/or cell shading on calculation sheet(s):
| red font | input
| blue font | calculated
| green font | fixed
| black font | set up, various
Run: | To copy the data from this file into the calculation spreadsheet: see Calculation spreadsheet, sheet: Method_input
Status: | Published | Files of version 2,30 from older date are compatible, but not all explanations are up-to-date
Main features: | This is a separate file with all input data that are needed for a calculation case, except the climatic data
In the calculation spreadsheet (sheet: Method_input) the name of this file can be filled in
and a macro can be started that copies all input data from this file into the calculation file
The calculation file can also be used directly, without separate input file,
but using the separate input files enables an easy change of cases and exchange of cases between users
To avoid incompatibility issues, the macro starts with checking whether the same version of input file and calculation file is used.
Time intervals and period: | See calculation file
Main limitations: | Not applicable for this file with Input data
Protection: | This file is protected against editing except for the cells where input is expected
The main reason is to prevent uncontrolled use and to keep technical support managable
More information:
CEN ISO/TR 52016-2, Energy performance of buildings
— Energy needs for heating and cooling, internal temperatures and sensible and latent heat loads
— Part 2: Explanation and justification of ISO 52016-1 and ISO 52017-1
Published June 2017
Links: | https://epb.center/documents/iso-52016-1/
includes also links to published articles and more
https://epb.center/documents/isotr-52016-2/
Overview of the meaning of each sheet in this file
Sheet |  | Description | Tab colour coding used to facilitate navigation:
INFO |  | Common info for all EPB spreadsheets, including DISCLAIMER | Red tab colour (do not touch) for INFO, Explanation and History
Explanation |  | Explanation on this spreadsheet on ISO 52016-1 / INPUT DATA
Method_input |  | Tabulated overview of all input data, according to common template for all EPB spreadsheets | Green tab colour for Method_input/calculation/output
Input_GrFl |  | Extra, integrated: Tabulated overview of all input data for ISO 13370 (ground floor th transmission), according to common template for all EPB spreadsheets | Yellow tab colour for extra sheets with I/O data or calculations
Input_0 |  | Input to control the calculation parameters, to fill the data for the building elements; plus processing to prepare the equations
Input_p |  | Input of hourly varying input data for conditions of use, copied from Use Profile Generator (based on EN 16798-1) | Formerly: weekly schedules (tabulated values)
CalcShad |  | Solar shading by obstacles and overhangs <to be integrated>
AdaptW |  | Special sheet: Windows with hourly adaptive thermal and solar properties (EN ISO 52016-3:2023 incl.draft Amd1)
History of this spreadsheet
Date | Developer | Description
2019.11.20 | Dick van Dijk | First version of separate input data file, published
2021-08-15 | Dick van Dijk | Updated version, following extensions and changes in the calculation tool
2023-01-06 | Dick van Dijk | Method_input: choice for adaptve comfort inserted. Input for AdaptW added
2023-01-16 | Dick van Dijk | All "No input" cells locked and sheets protected). Note: Input_p shall be unlocked to enable copy paste whole content from Use Profile Generator
2023-01-16 | Dick van Dijk | Published as test version
2023-09-21 | Dick van Dijk | Published. Input files of version 2,30 from older date are compatible, but not all explanations are up-to-date

## Method_input
XLS on ISO 52016-1 version | 2.3 | (to enable a check on compatibility of input data sets)
|  | Short id that will be used in XLS Calculation file after reading in these input data | BEST600
Only column D and column K are for input
Name | Symbol | Unit | value | Validity intervala | Originb | Varyingc | Calculation methodd | Symbol in origin (if different) | Notes | Notes on the specific input (optional)
General data on the assessed object and application (ISO 52016-1:2017, Table 11)
Space category for each space or group of spaces (if different from building category) | SPACECAT_TYPE | n/a | BESTEST |  | ISO 52000-1 | NO | H+M |  | Type is not (yet?) directly used
Calculation case | CASE_IDENTIFIER | n/a | 600 |  | ISO 52000-1 | NO | H+M
Description | - | - | Lightweight, continuous | Free text |  |  | H+M
Geometrical data list (ISO 52016-1:2017, Table 12)
Useful floor area of the thermal zone | Ause;zt | m2 | 48 |  |  |  | H+M
Air volume of the thermal zone | Vint;a;zt | m3 | 129.6 |  |  |  | H+M
Thermal zone related input data list (ISO 52016-1:2017, Table 13)
Areal thermal capacity of air and furniture per thermally conditioned zone (Hourly method!) | κm;int;a;zt = Cm;int;a;zi/Ause;zi | J/(m2·K) | 10000 | 0 to ∞ | Local or default (Table A.17) | No | H | -
Class of the internal heat capacity per thermally conditioned zone (Monthly method!) | - | - | 1 | Identifier | Local | No | M |  | ! Use number 1-> 5 for class very Light to Very heavy
INFO: this class number corresponds to the class description: | Very light
Building element related input data list (ISO 52016-1:2017, Table 14)
Overall heat transfer coefficient for the thermal bridges, per thermal zone (excl. ground floor which is covered in sheet "Input_GrFl") | Htr;tb;zt <excl. grfl> | W/K | 0 | 0 to ∞ | M2-5.1 | Yes | H+M | Htb
Input data related to conditions of use and technical building systems (ISO 52016-1:2017, Table 16)
Hourly calculation procedures:
Adaptive comfort criteria applied? | - | - | 0 | 0 or 1 | M1-6 | No | H |  | Calculated in Input_t; 'if =1: activated. If = 2: activated only during spring and autumn (see explanation, history)
Available heating power, per thermally conditioned zone, per hour | ΦH;avail;ztc;t | W | 100000 | 0 to ∞ | M3-1 | Yes | H
Available cooling power, per thermally conditioned zone, per hour | ΦC;avail;ztc;t | W | 100000 | 0 to ∞ | M4-1 | Yes | H | QC;out;zt,j
Convective fraction of the heating system per thermally conditioned zone (if system specific) (not usable for monthly method) | fH,c ztc | - | 1 | 0 to 1 | (M3-5 or M3 system description) or default (Table A.11) | No | H
Convective fraction of the cooling system per thermally conditioned zone (if system specific) (not usable for monthly method) | fC,c ztc | - | 1 | 0 to 1 | (M4-5 or M4 system description) or default (Table A.11) | No | H
Monthly calculation procedures:
The normal ('required thermal comfort level') heating temperature set-point per thermally conditioned zone (see also Notes in Clumn J ) | θint;set;H;ztc | °C | 20 | 0 to 50 | M1-6 | No | M |  | Manual input, to be matched with Input_p for hourly calculation
The reduced ('economy or low comfort level') heating temperature set-point of the zone (day, night and/or weekend) | θint;set;H;low;ztc | °C | 20 | 0 to 50 | M1-6 | No | M |  | Manual input, to be matched with Input_p for hourly calculation. In case of switch off use low value, e.g.: -999
The normal ('required thermal comfort level') cooling temperature set-point per thermally conditioned zone (see Notes) | θint;set;C;ztc | °C | 27 | 0 to 50 | M1-6 | No | M |  | Manual input, to be matched with Input_p for hourly calculation
Occupancy pattern (see Notes in column J ) | [8 empty] | These data could in theory be derived from the hourly pattern for hourly calculations. However, it is not just a simple counting of hours per day occupated vs non-occupated: if these hours are divided over different parts of the day, the number of periods per day and length per intermittency is different
The duration of the period with reduced heating set-point (y=night ) | ΔtH;red;y;ztc | h | 8 | 1 to 10 | M1-6 | No | M |  | ATTENTION: temperature can drop to low ('economy') temperature set point. set n to zero, not Δt!! Example input: resid: 7; office: 13
The number of repetitions in a week of reduction period (y=night) | nrep;H;red;y;ztc | - | 0 | 0 to 7 | M1-6 | No | M |  | Example input: resid: 7; office: 5
The duration of the period with reduced heating set-point (y=day) | ΔtH;red;y;ztc | h | 10 | 1 to 12 | M1-6 | No | M |  | Example input: resid: 11; office: 8
The number of repetitions in a week of reduction period (y=day) | nrep;H;red;y;ztc | - | 0 | 0 to 7 | M1-6 | No | M |  | Example input: resid:5; office:0
The duration of the period with reduced heating set-point (y=weekend) | ΔtH;red;y;ztc | h | 48 | 1 to 48 | M1-6 | No | M |  | Example input: resid: 48; office: 48
The number of repetitions in a week of reduction period (y=weekend) | nrep;H;red;y;ztc | - | 0 | 0 to 7 | M1-6 | No | M |  | Example input: resid:0; office:1
The number of hours during the weekend with reduced temperature set-point for cooling or interruption | ΔtC;red;wknd;ztc | - | 48 | 0 to 48 | M1-6 | No | M |  | set n to zero, not Δt!! Example input: resid: 48; office: 48
The number of repetitions in a week of this intermittency | nrep;C;red;wknd;ztc | - | 0 | 0 to 7 | M1-6 | No | M |  | Residential: 0; office: 1
Extra ventilation flow during cooling & comfort required hrs | φV;cool | m3/(h.m2) | 0 |  |  |  | M |  | During moderate and high occupancy
The fraction of sensible energy need to be added for dehumidification, per type of cooling system | fDHU;C;ss | - | 0.2 | 0 to 1 | M7-5 | No | M
Input data from ISO 52016-1:2017, Annex A / Annex B
Convective fraction of the internal gains into the zone | fint;c | - | 0.4 | 0 to 1 | Table A/B.11 | NO | H
Convective fraction of the solar radiation into the zone | fsol;c | - | 0.1 | 0 to 1 | Table A/B.12 | NO | H
Average difference between external air temperature and sky temperature | Δϑsky | K | 11 | -50 to +50 | H: Table A/B.19, M: Table A/B.31 | NO | H + M
Moisture absorption (positive value) or desorption (negative value) in materials in the zone | Gabs;ztc;t | kg/s | 0 | -∞ to ∞ | Table A/B.20 | NO | H
Dynamics correction factor for ventilation | fve;dyn;k | - | 1 | 0 to 1 | Table A/B.28 | NO | M |  | In this spreadsheet: one value for all vent.elements
Reference numerical parameter for the gain utilization factor | aH;0 | - | 1 | 0 to 1 | Table A/B.34 | NO | M
Reference time constant for the gain utilization factor | tH;0 | h | 15 | 0 to 100 | Table A/B.34 | NO | M
Reference numerical parameter for the loss utilization factor | aC;0 | - | 1 | 0 to 1 | Table A/B.35 | NO | M
Reference time constant for the loss utilization factor | tC;0 | h | 15 | 0 to 100 | Table A/B.35 | NO | M
Correlation factor for intermittent cooling | bC;red;wknd | - | 0.3 | 0 to 1 | Table A/B.37 | NO | M
Efficiency of latent heat recovery | ηHU;rvd | - | 0 | 0 to 1 | Table A/B.40 | NO | M
Annually accumulated amount of moisture to be supplied per kg dry air supply | Δx∙ta;sup | kg h/kg | 0.17 | 0 to ∞ | Table A/B.41 | NO | M
Special dynamics <work in progress>
Adaptive building envelope elements (draft EN ISO 52016-3) | EN-ISO_52016-3 |  | 0 | 0 or 1 |  |  | H
Coupling to ventilation air flow (EN 16798-7) demo active? | EN_16798-7 | - | 0 | 0 or 1 |  |  | H
Ventilative cooling (VCS) demo operative? | DynamVent | - | 0 | 0 or 1 |  |  | H |  | Used in sheet Input_t, uses special VCS sheet; if =1: set also input extra vent. for cooling in monthly calc.
Coupling to heat pump demo operative? | EN_15316-4-2 |  | 0 | 0 or 1 |  |  | H
Dynamic system operative? | DynSys |  | 0 | 0 or 1 |  |  | H

## Input_GrFl
Only column D and column I are for input
Name | Symbol | Unit | Value | Range | Origin | Varying | Notes | Notes on the specific input (optional)
Identifiers for building geometric characteristics | [6 empty] | ISO 13770:2017, Table 3
Area of floor | A | m2 | 0.00999 | ≥0 | — | No | Input in this spreadsheet is for floor type: slab-on-ground | Groundfloor
Exposed perimeter | P | m | 0.00999 | ≥0 | — | No |  | NOT APPLICABLE for BESTEST!!
Length of linear thermal bridge k | lk | m | n.a. | ≥0 | — | No | Erratum in the standard: this not an input in the standard... This is covered by the perimeter P
Thickness of the walls of the building | dw;e | m | 0.35 | ≥0 | — | No
Height of the upper surface of the floor above external ground level | h | m | n.a. | ≥0 |  | No | Not applicable for slab-on-ground floor
Depth of basement floor below ground level | z | m | n.a. | ≥0 |  | No | Not applicable for slab-on-ground floor
Identifiers for building boundary conditions | [6 empty] | ISO 13770:2017, Table 4
Annual mean internal temperature |  | °C | 23 | -50…+50 | ISO 52016-1 | No | Typically: the average between heating and cooling set point; see also next line (amplitude)
Amplitude of internal temperature variations |  | K | 3 | -50…+50 | ISO 52016-1 | No | = Half of the difference between the expected monthly max (e.g.: cooling set point) and monthly min (e.g.: heating set point)
Identifiers for periodic heat flows | [6 empty] | According to ISO 13370:2017, Annex H
Month number in which the minimum external temperature occurs | t | - | 1 | 1 or 7 | ISO 13370 Annex C | No | tau= 1 in the northern hemisphere and tau= 7 in the southern hemisphere.
Identifiers for thermal characteristics of building fabric | [6 empty] | ISO 13770:2017, Table 5
Linear thermal transmittance associated with wall/floor junction | Ψk | W/(m.K) | 0.05 | 0…10 | ISO 14683 or ISO 10211 | No
Thermal properties of the ground | [6 empty] | ISO 13770:2017, Table 7
Heat capacity of ground per volume | ρc | J/(m3·K) | 2000000 | 1...4 106 | ISO 13370, Table 7 | No | Default value (ISO 13370, Table 7, Table B.4)
Thermal properties of building materials
Thermal resistance of the floor construction (excluding the effect of the ground) | Rf | (m2.K)/W | 5.3 | 0...10 | ISO 13370 | No | ISO 13770:2017, 6.4.2 | test note last input

## Input_0
| Time independent input data per building element |  | NOTE: Several input data are given in "Method_input" sheet, but still shown here, for the simple reason that the macro | [9 empty] | On this sheet:
| See sheet Method_input for general explanation on this file with input data |  | reads values from fixed cell positions in this sheet, So in the "Method_input" sheet rows may be reorganised, | [9 empty] | Input according to ISO 52016-1:2017, 6.5.7 and 6.5.8
while this sheet remains uncorrupted
[12 empty] | Class id. | Class | Monthly method, internal capacity, Cm;int;eff;ztc /Ag | Hourly method, specific heat capacity of opaque elements, κm;op
[14 empty] | J/(m2·K) | J/(m2·K)
[12 empty] | 1 | Very light | 80000 | 50000
[12 empty] | 2 | Light | 110000 | 75000
[12 empty] | 3 | Medium | 165000 | 110000
[12 empty] | 4 | Heavy | 260000 | 175000
[8 empty] | Explanation of element types: |  |  |  | 5 | Very heavy | 370000 | 250000
[8 empty] | (Sub-)types: | Description |  |  |  |  | Table 21 | Table A/B.14
[8 empty] | OP | Opaque, External environment
[8 empty] | W | Window or door, External environment
[8 empty] | GR | Ground ->>>!ATTENTION: requires extra input in sheet input_GrFl; Af and Rf;eff to be manually copied from sheet calc_GrFl to this sheet
[8 empty] | AD | Adiabatic; (assuming symmetry): use input for half of the element!! ATTENTION: a_sol and input for IR_sky (Fsky) need to be set to zero; hce and hre are ignored
[8 empty] | NA | Not available: if this type is detected this plus all next elements are ignored
Class
[8 empty] | for OP, AD, GR: | I, E, IE, M or D: th.capacity by approximation near Internal surface, near External surface, both I and E, near Middle or evenly Distributed
| ATTENTION: for ground floor: | [6 empty] | for W: | If special dynamics is active: F(fixed), or assign group Wadapt1, Wadapt2 with variable props and control strategy in special sheet EN-ISO_52016-3
| Rc;eli_inp = Rf;eff (to be copied manually from sheet "Calc_GrFl", Cell D11) | [7 empty] | If Wadapti: the fixed values in this sheet Input_0 will still be used for the monthly method, to calculate the monthly heat transfer and gains | If V1 or V2: the fixed values in this sheet Input_0 will still be used for the monthly method, to calculate the monthly heat transfer and gains
Row nr per element | Data per element | Eli |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Sums or sumproducts |  |  |  | Notes on the specific input (optional)
0 | Comment | Name | Unit | ground fl - as external element | wall S | window S | wall E | wall W | wall N | flat roof | dummy | dummy | dummy | dummy | dummy | dummy | dummy | dummy | dummy | dummy | dummy | dummy | dummy
1 | Explan. in table above | Subtype | - | OP | OP | W | OP | OP | OP | OP | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
2 |  | Class | - | I | D | F | D | D | D | D | D | D | D | D | D | D | D | D | D | D | D | D | D
3 | !!!! Per element: input either U or R!! Attention: in this spreadsheet U-value of windows is based on window area (incl.frame) | Ueli_inp | W/(m2K) |  |  | 2.984 |  |  |  |  | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8
4 | !!!! (so: keep one row empty!!) | Class: Rc;eli_inp; -: (m2K)/W; I: 25.254; D: 1.79; D: 1.789; D: 1.789; D: 1.789; D: 2.992
5 | if opq or floor (but actual calc. in this spreadsheet is more flexible: values are used for each node!) | κm;eli | J/(m2K) | 50000 | 50000 | 0 | 50000 | 50000 | 50000 | 50000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Area shall be set to zero if "NA"
6 | Attention: in this spreadsheet, if transparent: window area (incl.frame) | Aeli | m2 | 48 | 9.6 | 12 | 16.2 | 16.2 | 21.6 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.6 | Aeli;tot | m2 | Used in macro
7 | if opq (but actual calc. in this spreadsheet is more flexible: values are used for each node!) | asol;eli | - | 0 | 0.6 | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Area shall be set to zero if "NA"
8 | if transparant Attention: in this spreadsheet g-value is based on window area (incl.frame) | gw;eli | - | 0 | 0 | 0.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Columns for chosen Or. and Tilt shall be made available in sheet ClimData! | Orientation and tilt | For example SV, S45, EV, E30, NV, WV,W135, etc. and e.g. HOR | HOR | SV | SV | EV | WV | NV | HOR | SV | SV | SV | SV | SV | SV | SV | SV | SV | SV | SV | SV | SV
10 |  | (void row) | (void row)
11 |  | hci;eli | W/(m2K) | 0.7 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 462.6 | Σ(Aeli*hci;eli) | W/(m2K), W/K | Used in macro
12 |  | hri;eli | W/(m2K) | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | hri;elk;mn=Σ(Aelk/Aeli;tot)*hri;elk | W/(m2K) | Used in macro
13 | hce and hre are ignored for ground floor (but avoid zero values) | hce;eli | W/(m2K) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | !! For gr.floor: Hce, hre are ignored, but do not enter zero's
14 |  | hre;eli | W/(m2K) | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14
15 | View factor between eli and sky | Fsk;eli | - | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
16 | For hrly calculation: solar shading by obstacle number (1) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Select number on sheet Calc_shade (in preparation)
17 | For hrly calculation: solar shading by obstacle number (2) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | For hrly calculation: solar shading by overhang number |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | For mnthly calculation: direct shading reduction factor number |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20

## Input_p
Source data sheet | BESTEST600 | Explanation in Use Profile Generator - Result sheet
| Manually adapted from SOFF | This sheet allows you to easily extract a combinastion of the profiles that you generated in the "Profile_16798_1_Base" sheet
Space area (m2) | 48 | Input the desired data in the sheets "Calendar", "Profile_16798_1_base"
Space volume (m3) | 0 | Select the desired data in the drop-down menus of the yellow cells, in the desired order so that you can copy paste a single block into your destination file
Comfort category | II | --> NOTE: blank columns are not allowed. Data extraction automatically stops when the first blank heading is found
Type of building | Low polluting | Clear previous data with the "Clear data" button
Ventilation calculation option | Method 1 - Perceived IAQ | Get your custom data-set with the "Get updated data" button
To copy to destination Excel file: (1): Select all, Copy. (2): In destination file: Paste values (!) in cell A1
[8 empty] | Ad hoc manual input | Not used | Ad hoc formula for this case! | Ad hoc manual input | Ad hoc manual input |  | Ad hoc formula for this case! | Ad hoc formula for this case! | Ad hoc manual input |  |  | Ad hoc manual input | Ad hoc manual input | Ad hoc manual input | Ad hoc manual input | Ad hoc manual input
| Column reference | 22 | 42 | 10 | 40 | 39 | 9 | 11 | 63 | 17 | 18 | 19 | 21 | 16 | 31 | 32 | 35 | 36 | 52 | 48 | 45 | 46 | 49 | 0 | 0 | 0
| Data | Calculation interval 1 - based | Hour of year 1 - based | Month | Hour of day 1 - based | Day of year - 1 based | Date | Type of day | Occupants density p/m² | Hsys;op ID | Csys;op ID | Vsys;op ID | HU/DHU op ID | Comfort required ID | θint set for heating °C | θint set for cooling °C | HU set % RH | DHU set % RH | Ventilation flow rate l/sm² | Persons sensible gains W/m² | Appliances sensible gains W/m² | Light W/m² | Vapour production g/hm² |  |  |  | <-- select on this row the data that you want to prepare
| Units | # | # | # | # | # | dd/mm/yyyy | ID | p/m² | ID | ID | ID | ID | ID | °C | °C | % RH | % RH | l/sm² | W/m² | W/m² | W/m² | g/hm²
| Year total | [6 empty] | p/m²: 273.75; ID: 17520; l/sm²: 2693.7; W/m²: 0; W/m²: 36500; W/m²: 0; g/hm²: 0
| Average | [6 empty] | p/m²: 0.03125; ID: 2; l/sm²: 0.3075; W/m²: 0; W/m²: 4.1667; W/m²: 0; g/hm²: 0
|  | 1 | -743 | Pre | 1 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2 | -742 | Pre | 2 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3 | -741 | Pre | 3 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4 | -740 | Pre | 4 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5 | -739 | Pre | 5 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6 | -738 | Pre | 6 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7 | -737 | Pre | 7 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8 | -736 | Pre | 8 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9 | -735 | Pre | 9 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 10 | -734 | Pre | 10 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 11 | -733 | Pre | 11 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 12 | -732 | Pre | 12 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 13 | -731 | Pre | 13 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 14 | -730 | Pre | 14 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 15 | -729 | Pre | 15 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 16 | -728 | Pre | 16 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 17 | -727 | Pre | 17 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 18 | -726 | Pre | 18 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 19 | -725 | Pre | 19 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 20 | -724 | Pre | 20 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 21 | -723 | Pre | 21 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 22 | -722 | Pre | 22 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 23 | -721 | Pre | 23 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 24 | -720 | Pre | 24 | -30 | 43070 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 25 | -719 | Pre | 1 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 26 | -718 | Pre | 2 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 27 | -717 | Pre | 3 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 28 | -716 | Pre | 4 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 29 | -715 | Pre | 5 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 30 | -714 | Pre | 6 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 31 | -713 | Pre | 7 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 32 | -712 | Pre | 8 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 33 | -711 | Pre | 9 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 34 | -710 | Pre | 10 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 35 | -709 | Pre | 11 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 36 | -708 | Pre | 12 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 37 | -707 | Pre | 13 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 38 | -706 | Pre | 14 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 39 | -705 | Pre | 15 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 40 | -704 | Pre | 16 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 41 | -703 | Pre | 17 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 42 | -702 | Pre | 18 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 43 | -701 | Pre | 19 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 44 | -700 | Pre | 20 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 45 | -699 | Pre | 21 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 46 | -698 | Pre | 22 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 47 | -697 | Pre | 23 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 48 | -696 | Pre | 24 | -29 | 43071 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 49 | -695 | Pre | 1 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 50 | -694 | Pre | 2 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 51 | -693 | Pre | 3 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 52 | -692 | Pre | 4 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 53 | -691 | Pre | 5 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 54 | -690 | Pre | 6 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 55 | -689 | Pre | 7 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 56 | -688 | Pre | 8 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 57 | -687 | Pre | 9 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 58 | -686 | Pre | 10 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 59 | -685 | Pre | 11 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 60 | -684 | Pre | 12 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 61 | -683 | Pre | 13 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 62 | -682 | Pre | 14 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 63 | -681 | Pre | 15 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 64 | -680 | Pre | 16 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 65 | -679 | Pre | 17 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 66 | -678 | Pre | 18 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 67 | -677 | Pre | 19 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 68 | -676 | Pre | 20 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 69 | -675 | Pre | 21 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 70 | -674 | Pre | 22 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 71 | -673 | Pre | 23 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 72 | -672 | Pre | 24 | -28 | 43072 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 73 | -671 | Pre | 1 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 74 | -670 | Pre | 2 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 75 | -669 | Pre | 3 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 76 | -668 | Pre | 4 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 77 | -667 | Pre | 5 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 78 | -666 | Pre | 6 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 79 | -665 | Pre | 7 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 80 | -664 | Pre | 8 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 81 | -663 | Pre | 9 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 82 | -662 | Pre | 10 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 83 | -661 | Pre | 11 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 84 | -660 | Pre | 12 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 85 | -659 | Pre | 13 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 86 | -658 | Pre | 14 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 87 | -657 | Pre | 15 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 88 | -656 | Pre | 16 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 89 | -655 | Pre | 17 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 90 | -654 | Pre | 18 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 91 | -653 | Pre | 19 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 92 | -652 | Pre | 20 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 93 | -651 | Pre | 21 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 94 | -650 | Pre | 22 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 95 | -649 | Pre | 23 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 96 | -648 | Pre | 24 | -27 | 43073 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 97 | -647 | Pre | 1 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 98 | -646 | Pre | 2 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 99 | -645 | Pre | 3 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 100 | -644 | Pre | 4 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 101 | -643 | Pre | 5 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 102 | -642 | Pre | 6 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 103 | -641 | Pre | 7 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 104 | -640 | Pre | 8 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 105 | -639 | Pre | 9 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 106 | -638 | Pre | 10 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 107 | -637 | Pre | 11 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 108 | -636 | Pre | 12 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 109 | -635 | Pre | 13 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 110 | -634 | Pre | 14 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 111 | -633 | Pre | 15 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 112 | -632 | Pre | 16 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 113 | -631 | Pre | 17 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 114 | -630 | Pre | 18 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 115 | -629 | Pre | 19 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 116 | -628 | Pre | 20 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 117 | -627 | Pre | 21 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 118 | -626 | Pre | 22 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 119 | -625 | Pre | 23 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 120 | -624 | Pre | 24 | -26 | 43074 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 121 | -623 | Pre | 1 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 122 | -622 | Pre | 2 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 123 | -621 | Pre | 3 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 124 | -620 | Pre | 4 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 125 | -619 | Pre | 5 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 126 | -618 | Pre | 6 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 127 | -617 | Pre | 7 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 128 | -616 | Pre | 8 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 129 | -615 | Pre | 9 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 130 | -614 | Pre | 10 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 131 | -613 | Pre | 11 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 132 | -612 | Pre | 12 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 133 | -611 | Pre | 13 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 134 | -610 | Pre | 14 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 135 | -609 | Pre | 15 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 136 | -608 | Pre | 16 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 137 | -607 | Pre | 17 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 138 | -606 | Pre | 18 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 139 | -605 | Pre | 19 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 140 | -604 | Pre | 20 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 141 | -603 | Pre | 21 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 142 | -602 | Pre | 22 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 143 | -601 | Pre | 23 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 144 | -600 | Pre | 24 | -25 | 43075 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 145 | -599 | Pre | 1 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 146 | -598 | Pre | 2 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 147 | -597 | Pre | 3 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 148 | -596 | Pre | 4 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 149 | -595 | Pre | 5 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 150 | -594 | Pre | 6 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 151 | -593 | Pre | 7 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 152 | -592 | Pre | 8 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 153 | -591 | Pre | 9 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 154 | -590 | Pre | 10 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 155 | -589 | Pre | 11 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 156 | -588 | Pre | 12 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 157 | -587 | Pre | 13 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 158 | -586 | Pre | 14 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 159 | -585 | Pre | 15 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 160 | -584 | Pre | 16 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 161 | -583 | Pre | 17 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 162 | -582 | Pre | 18 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 163 | -581 | Pre | 19 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 164 | -580 | Pre | 20 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 165 | -579 | Pre | 21 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 166 | -578 | Pre | 22 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 167 | -577 | Pre | 23 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 168 | -576 | Pre | 24 | -24 | 43076 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 169 | -575 | Pre | 1 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 170 | -574 | Pre | 2 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 171 | -573 | Pre | 3 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 172 | -572 | Pre | 4 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 173 | -571 | Pre | 5 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 174 | -570 | Pre | 6 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 175 | -569 | Pre | 7 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 176 | -568 | Pre | 8 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 177 | -567 | Pre | 9 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 178 | -566 | Pre | 10 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 179 | -565 | Pre | 11 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 180 | -564 | Pre | 12 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 181 | -563 | Pre | 13 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 182 | -562 | Pre | 14 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 183 | -561 | Pre | 15 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 184 | -560 | Pre | 16 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 185 | -559 | Pre | 17 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 186 | -558 | Pre | 18 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 187 | -557 | Pre | 19 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 188 | -556 | Pre | 20 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 189 | -555 | Pre | 21 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 190 | -554 | Pre | 22 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 191 | -553 | Pre | 23 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 192 | -552 | Pre | 24 | -23 | 43077 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 193 | -551 | Pre | 1 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 194 | -550 | Pre | 2 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 195 | -549 | Pre | 3 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 196 | -548 | Pre | 4 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 197 | -547 | Pre | 5 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 198 | -546 | Pre | 6 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 199 | -545 | Pre | 7 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 200 | -544 | Pre | 8 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 201 | -543 | Pre | 9 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 202 | -542 | Pre | 10 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 203 | -541 | Pre | 11 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 204 | -540 | Pre | 12 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 205 | -539 | Pre | 13 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 206 | -538 | Pre | 14 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 207 | -537 | Pre | 15 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 208 | -536 | Pre | 16 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 209 | -535 | Pre | 17 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 210 | -534 | Pre | 18 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 211 | -533 | Pre | 19 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 212 | -532 | Pre | 20 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 213 | -531 | Pre | 21 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 214 | -530 | Pre | 22 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 215 | -529 | Pre | 23 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 216 | -528 | Pre | 24 | -22 | 43078 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 217 | -527 | Pre | 1 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 218 | -526 | Pre | 2 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 219 | -525 | Pre | 3 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 220 | -524 | Pre | 4 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 221 | -523 | Pre | 5 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 222 | -522 | Pre | 6 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 223 | -521 | Pre | 7 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 224 | -520 | Pre | 8 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 225 | -519 | Pre | 9 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 226 | -518 | Pre | 10 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 227 | -517 | Pre | 11 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 228 | -516 | Pre | 12 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 229 | -515 | Pre | 13 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 230 | -514 | Pre | 14 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 231 | -513 | Pre | 15 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 232 | -512 | Pre | 16 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 233 | -511 | Pre | 17 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 234 | -510 | Pre | 18 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 235 | -509 | Pre | 19 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 236 | -508 | Pre | 20 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 237 | -507 | Pre | 21 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 238 | -506 | Pre | 22 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 239 | -505 | Pre | 23 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 240 | -504 | Pre | 24 | -21 | 43079 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 241 | -503 | Pre | 1 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 242 | -502 | Pre | 2 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 243 | -501 | Pre | 3 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 244 | -500 | Pre | 4 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 245 | -499 | Pre | 5 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 246 | -498 | Pre | 6 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 247 | -497 | Pre | 7 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 248 | -496 | Pre | 8 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 249 | -495 | Pre | 9 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 250 | -494 | Pre | 10 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 251 | -493 | Pre | 11 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 252 | -492 | Pre | 12 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 253 | -491 | Pre | 13 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 254 | -490 | Pre | 14 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 255 | -489 | Pre | 15 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 256 | -488 | Pre | 16 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 257 | -487 | Pre | 17 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 258 | -486 | Pre | 18 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 259 | -485 | Pre | 19 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 260 | -484 | Pre | 20 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 261 | -483 | Pre | 21 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 262 | -482 | Pre | 22 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 263 | -481 | Pre | 23 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 264 | -480 | Pre | 24 | -20 | 43080 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 265 | -479 | Pre | 1 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 266 | -478 | Pre | 2 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 267 | -477 | Pre | 3 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 268 | -476 | Pre | 4 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 269 | -475 | Pre | 5 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 270 | -474 | Pre | 6 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 271 | -473 | Pre | 7 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 272 | -472 | Pre | 8 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 273 | -471 | Pre | 9 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 274 | -470 | Pre | 10 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 275 | -469 | Pre | 11 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 276 | -468 | Pre | 12 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 277 | -467 | Pre | 13 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 278 | -466 | Pre | 14 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 279 | -465 | Pre | 15 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 280 | -464 | Pre | 16 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 281 | -463 | Pre | 17 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 282 | -462 | Pre | 18 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 283 | -461 | Pre | 19 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 284 | -460 | Pre | 20 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 285 | -459 | Pre | 21 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 286 | -458 | Pre | 22 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 287 | -457 | Pre | 23 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 288 | -456 | Pre | 24 | -19 | 43081 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 289 | -455 | Pre | 1 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 290 | -454 | Pre | 2 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 291 | -453 | Pre | 3 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 292 | -452 | Pre | 4 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 293 | -451 | Pre | 5 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 294 | -450 | Pre | 6 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 295 | -449 | Pre | 7 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 296 | -448 | Pre | 8 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 297 | -447 | Pre | 9 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 298 | -446 | Pre | 10 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 299 | -445 | Pre | 11 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 300 | -444 | Pre | 12 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 301 | -443 | Pre | 13 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 302 | -442 | Pre | 14 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 303 | -441 | Pre | 15 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 304 | -440 | Pre | 16 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 305 | -439 | Pre | 17 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 306 | -438 | Pre | 18 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 307 | -437 | Pre | 19 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 308 | -436 | Pre | 20 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 309 | -435 | Pre | 21 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 310 | -434 | Pre | 22 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 311 | -433 | Pre | 23 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 312 | -432 | Pre | 24 | -18 | 43082 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 313 | -431 | Pre | 1 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 314 | -430 | Pre | 2 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 315 | -429 | Pre | 3 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 316 | -428 | Pre | 4 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 317 | -427 | Pre | 5 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 318 | -426 | Pre | 6 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 319 | -425 | Pre | 7 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 320 | -424 | Pre | 8 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 321 | -423 | Pre | 9 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 322 | -422 | Pre | 10 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 323 | -421 | Pre | 11 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 324 | -420 | Pre | 12 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 325 | -419 | Pre | 13 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 326 | -418 | Pre | 14 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 327 | -417 | Pre | 15 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 328 | -416 | Pre | 16 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 329 | -415 | Pre | 17 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 330 | -414 | Pre | 18 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 331 | -413 | Pre | 19 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 332 | -412 | Pre | 20 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 333 | -411 | Pre | 21 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 334 | -410 | Pre | 22 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 335 | -409 | Pre | 23 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 336 | -408 | Pre | 24 | -17 | 43083 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 337 | -407 | Pre | 1 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 338 | -406 | Pre | 2 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 339 | -405 | Pre | 3 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 340 | -404 | Pre | 4 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 341 | -403 | Pre | 5 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 342 | -402 | Pre | 6 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 343 | -401 | Pre | 7 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 344 | -400 | Pre | 8 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 345 | -399 | Pre | 9 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 346 | -398 | Pre | 10 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 347 | -397 | Pre | 11 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 348 | -396 | Pre | 12 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 349 | -395 | Pre | 13 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 350 | -394 | Pre | 14 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 351 | -393 | Pre | 15 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 352 | -392 | Pre | 16 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 353 | -391 | Pre | 17 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 354 | -390 | Pre | 18 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 355 | -389 | Pre | 19 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 356 | -388 | Pre | 20 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 357 | -387 | Pre | 21 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 358 | -386 | Pre | 22 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 359 | -385 | Pre | 23 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 360 | -384 | Pre | 24 | -16 | 43084 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 361 | -383 | Pre | 1 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 362 | -382 | Pre | 2 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 363 | -381 | Pre | 3 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 364 | -380 | Pre | 4 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 365 | -379 | Pre | 5 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 366 | -378 | Pre | 6 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 367 | -377 | Pre | 7 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 368 | -376 | Pre | 8 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 369 | -375 | Pre | 9 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 370 | -374 | Pre | 10 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 371 | -373 | Pre | 11 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 372 | -372 | Pre | 12 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 373 | -371 | Pre | 13 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 374 | -370 | Pre | 14 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 375 | -369 | Pre | 15 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 376 | -368 | Pre | 16 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 377 | -367 | Pre | 17 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 378 | -366 | Pre | 18 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 379 | -365 | Pre | 19 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 380 | -364 | Pre | 20 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 381 | -363 | Pre | 21 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 382 | -362 | Pre | 22 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 383 | -361 | Pre | 23 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 384 | -360 | Pre | 24 | -15 | 43085 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 385 | -359 | Pre | 1 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 386 | -358 | Pre | 2 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 387 | -357 | Pre | 3 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 388 | -356 | Pre | 4 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 389 | -355 | Pre | 5 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 390 | -354 | Pre | 6 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 391 | -353 | Pre | 7 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 392 | -352 | Pre | 8 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 393 | -351 | Pre | 9 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 394 | -350 | Pre | 10 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 395 | -349 | Pre | 11 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 396 | -348 | Pre | 12 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 397 | -347 | Pre | 13 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 398 | -346 | Pre | 14 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 399 | -345 | Pre | 15 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 400 | -344 | Pre | 16 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 401 | -343 | Pre | 17 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 402 | -342 | Pre | 18 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 403 | -341 | Pre | 19 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 404 | -340 | Pre | 20 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 405 | -339 | Pre | 21 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 406 | -338 | Pre | 22 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 407 | -337 | Pre | 23 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 408 | -336 | Pre | 24 | -14 | 43086 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 409 | -335 | Pre | 1 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 410 | -334 | Pre | 2 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 411 | -333 | Pre | 3 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 412 | -332 | Pre | 4 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 413 | -331 | Pre | 5 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 414 | -330 | Pre | 6 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 415 | -329 | Pre | 7 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 416 | -328 | Pre | 8 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 417 | -327 | Pre | 9 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 418 | -326 | Pre | 10 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 419 | -325 | Pre | 11 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 420 | -324 | Pre | 12 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 421 | -323 | Pre | 13 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 422 | -322 | Pre | 14 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 423 | -321 | Pre | 15 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 424 | -320 | Pre | 16 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 425 | -319 | Pre | 17 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 426 | -318 | Pre | 18 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 427 | -317 | Pre | 19 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 428 | -316 | Pre | 20 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 429 | -315 | Pre | 21 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 430 | -314 | Pre | 22 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 431 | -313 | Pre | 23 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 432 | -312 | Pre | 24 | -13 | 43087 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 433 | -311 | Pre | 1 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 434 | -310 | Pre | 2 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 435 | -309 | Pre | 3 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 436 | -308 | Pre | 4 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 437 | -307 | Pre | 5 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 438 | -306 | Pre | 6 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 439 | -305 | Pre | 7 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 440 | -304 | Pre | 8 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 441 | -303 | Pre | 9 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 442 | -302 | Pre | 10 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 443 | -301 | Pre | 11 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 444 | -300 | Pre | 12 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 445 | -299 | Pre | 13 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 446 | -298 | Pre | 14 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 447 | -297 | Pre | 15 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 448 | -296 | Pre | 16 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 449 | -295 | Pre | 17 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 450 | -294 | Pre | 18 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 451 | -293 | Pre | 19 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 452 | -292 | Pre | 20 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 453 | -291 | Pre | 21 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 454 | -290 | Pre | 22 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 455 | -289 | Pre | 23 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 456 | -288 | Pre | 24 | -12 | 43088 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 457 | -287 | Pre | 1 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 458 | -286 | Pre | 2 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 459 | -285 | Pre | 3 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 460 | -284 | Pre | 4 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 461 | -283 | Pre | 5 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 462 | -282 | Pre | 6 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 463 | -281 | Pre | 7 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 464 | -280 | Pre | 8 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 465 | -279 | Pre | 9 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 466 | -278 | Pre | 10 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 467 | -277 | Pre | 11 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 468 | -276 | Pre | 12 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 469 | -275 | Pre | 13 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 470 | -274 | Pre | 14 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 471 | -273 | Pre | 15 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 472 | -272 | Pre | 16 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 473 | -271 | Pre | 17 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 474 | -270 | Pre | 18 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 475 | -269 | Pre | 19 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 476 | -268 | Pre | 20 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 477 | -267 | Pre | 21 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 478 | -266 | Pre | 22 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 479 | -265 | Pre | 23 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 480 | -264 | Pre | 24 | -11 | 43089 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 481 | -263 | Pre | 1 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 482 | -262 | Pre | 2 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 483 | -261 | Pre | 3 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 484 | -260 | Pre | 4 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 485 | -259 | Pre | 5 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 486 | -258 | Pre | 6 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 487 | -257 | Pre | 7 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 488 | -256 | Pre | 8 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 489 | -255 | Pre | 9 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 490 | -254 | Pre | 10 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 491 | -253 | Pre | 11 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 492 | -252 | Pre | 12 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 493 | -251 | Pre | 13 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 494 | -250 | Pre | 14 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 495 | -249 | Pre | 15 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 496 | -248 | Pre | 16 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 497 | -247 | Pre | 17 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 498 | -246 | Pre | 18 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 499 | -245 | Pre | 19 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 500 | -244 | Pre | 20 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 501 | -243 | Pre | 21 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 502 | -242 | Pre | 22 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 503 | -241 | Pre | 23 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 504 | -240 | Pre | 24 | -10 | 43090 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 505 | -239 | Pre | 1 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 506 | -238 | Pre | 2 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 507 | -237 | Pre | 3 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 508 | -236 | Pre | 4 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 509 | -235 | Pre | 5 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 510 | -234 | Pre | 6 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 511 | -233 | Pre | 7 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 512 | -232 | Pre | 8 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 513 | -231 | Pre | 9 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 514 | -230 | Pre | 10 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 515 | -229 | Pre | 11 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 516 | -228 | Pre | 12 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 517 | -227 | Pre | 13 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 518 | -226 | Pre | 14 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 519 | -225 | Pre | 15 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 520 | -224 | Pre | 16 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 521 | -223 | Pre | 17 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 522 | -222 | Pre | 18 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 523 | -221 | Pre | 19 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 524 | -220 | Pre | 20 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 525 | -219 | Pre | 21 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 526 | -218 | Pre | 22 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 527 | -217 | Pre | 23 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 528 | -216 | Pre | 24 | -9 | 43091 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 529 | -215 | Pre | 1 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 530 | -214 | Pre | 2 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 531 | -213 | Pre | 3 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 532 | -212 | Pre | 4 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 533 | -211 | Pre | 5 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 534 | -210 | Pre | 6 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 535 | -209 | Pre | 7 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 536 | -208 | Pre | 8 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 537 | -207 | Pre | 9 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 538 | -206 | Pre | 10 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 539 | -205 | Pre | 11 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 540 | -204 | Pre | 12 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 541 | -203 | Pre | 13 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 542 | -202 | Pre | 14 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 543 | -201 | Pre | 15 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 544 | -200 | Pre | 16 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 545 | -199 | Pre | 17 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 546 | -198 | Pre | 18 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 547 | -197 | Pre | 19 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 548 | -196 | Pre | 20 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 549 | -195 | Pre | 21 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 550 | -194 | Pre | 22 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 551 | -193 | Pre | 23 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 552 | -192 | Pre | 24 | -8 | 43092 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 553 | -191 | Pre | 1 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 554 | -190 | Pre | 2 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 555 | -189 | Pre | 3 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 556 | -188 | Pre | 4 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 557 | -187 | Pre | 5 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 558 | -186 | Pre | 6 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 559 | -185 | Pre | 7 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 560 | -184 | Pre | 8 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 561 | -183 | Pre | 9 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 562 | -182 | Pre | 10 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 563 | -181 | Pre | 11 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 564 | -180 | Pre | 12 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 565 | -179 | Pre | 13 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 566 | -178 | Pre | 14 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 567 | -177 | Pre | 15 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 568 | -176 | Pre | 16 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 569 | -175 | Pre | 17 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 570 | -174 | Pre | 18 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 571 | -173 | Pre | 19 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 572 | -172 | Pre | 20 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 573 | -171 | Pre | 21 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 574 | -170 | Pre | 22 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 575 | -169 | Pre | 23 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 576 | -168 | Pre | 24 | -7 | 43093 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 577 | -167 | Pre | 1 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 578 | -166 | Pre | 2 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 579 | -165 | Pre | 3 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 580 | -164 | Pre | 4 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 581 | -163 | Pre | 5 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 582 | -162 | Pre | 6 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 583 | -161 | Pre | 7 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 584 | -160 | Pre | 8 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 585 | -159 | Pre | 9 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 586 | -158 | Pre | 10 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 587 | -157 | Pre | 11 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 588 | -156 | Pre | 12 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 589 | -155 | Pre | 13 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 590 | -154 | Pre | 14 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 591 | -153 | Pre | 15 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 592 | -152 | Pre | 16 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 593 | -151 | Pre | 17 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 594 | -150 | Pre | 18 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 595 | -149 | Pre | 19 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 596 | -148 | Pre | 20 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 597 | -147 | Pre | 21 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 598 | -146 | Pre | 22 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 599 | -145 | Pre | 23 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 600 | -144 | Pre | 24 | -6 | 43094 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 601 | -143 | Pre | 1 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 602 | -142 | Pre | 2 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 603 | -141 | Pre | 3 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 604 | -140 | Pre | 4 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 605 | -139 | Pre | 5 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 606 | -138 | Pre | 6 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 607 | -137 | Pre | 7 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 608 | -136 | Pre | 8 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 609 | -135 | Pre | 9 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 610 | -134 | Pre | 10 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 611 | -133 | Pre | 11 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 612 | -132 | Pre | 12 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 613 | -131 | Pre | 13 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 614 | -130 | Pre | 14 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 615 | -129 | Pre | 15 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 616 | -128 | Pre | 16 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 617 | -127 | Pre | 17 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 618 | -126 | Pre | 18 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 619 | -125 | Pre | 19 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 620 | -124 | Pre | 20 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 621 | -123 | Pre | 21 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 622 | -122 | Pre | 22 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 623 | -121 | Pre | 23 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 624 | -120 | Pre | 24 | -5 | 43095 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 625 | -119 | Pre | 1 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 626 | -118 | Pre | 2 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 627 | -117 | Pre | 3 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 628 | -116 | Pre | 4 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 629 | -115 | Pre | 5 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 630 | -114 | Pre | 6 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 631 | -113 | Pre | 7 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 632 | -112 | Pre | 8 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 633 | -111 | Pre | 9 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 634 | -110 | Pre | 10 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 635 | -109 | Pre | 11 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 636 | -108 | Pre | 12 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 637 | -107 | Pre | 13 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 638 | -106 | Pre | 14 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 639 | -105 | Pre | 15 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 640 | -104 | Pre | 16 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 641 | -103 | Pre | 17 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 642 | -102 | Pre | 18 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 643 | -101 | Pre | 19 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 644 | -100 | Pre | 20 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 645 | -99 | Pre | 21 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 646 | -98 | Pre | 22 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 647 | -97 | Pre | 23 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 648 | -96 | Pre | 24 | -4 | 43096 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 649 | -95 | Pre | 1 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 650 | -94 | Pre | 2 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 651 | -93 | Pre | 3 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 652 | -92 | Pre | 4 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 653 | -91 | Pre | 5 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 654 | -90 | Pre | 6 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 655 | -89 | Pre | 7 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 656 | -88 | Pre | 8 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 657 | -87 | Pre | 9 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 658 | -86 | Pre | 10 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 659 | -85 | Pre | 11 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 660 | -84 | Pre | 12 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 661 | -83 | Pre | 13 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 662 | -82 | Pre | 14 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 663 | -81 | Pre | 15 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 664 | -80 | Pre | 16 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 665 | -79 | Pre | 17 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 666 | -78 | Pre | 18 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 667 | -77 | Pre | 19 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 668 | -76 | Pre | 20 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 669 | -75 | Pre | 21 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 670 | -74 | Pre | 22 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 671 | -73 | Pre | 23 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 672 | -72 | Pre | 24 | -3 | 43097 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 673 | -71 | Pre | 1 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 674 | -70 | Pre | 2 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 675 | -69 | Pre | 3 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 676 | -68 | Pre | 4 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 677 | -67 | Pre | 5 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 678 | -66 | Pre | 6 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 679 | -65 | Pre | 7 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 680 | -64 | Pre | 8 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 681 | -63 | Pre | 9 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 682 | -62 | Pre | 10 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 683 | -61 | Pre | 11 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 684 | -60 | Pre | 12 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 685 | -59 | Pre | 13 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 686 | -58 | Pre | 14 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 687 | -57 | Pre | 15 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 688 | -56 | Pre | 16 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 689 | -55 | Pre | 17 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 690 | -54 | Pre | 18 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 691 | -53 | Pre | 19 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 692 | -52 | Pre | 20 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 693 | -51 | Pre | 21 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 694 | -50 | Pre | 22 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 695 | -49 | Pre | 23 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 696 | -48 | Pre | 24 | -2 | 43098 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 697 | -47 | Pre | 1 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 698 | -46 | Pre | 2 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 699 | -45 | Pre | 3 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 700 | -44 | Pre | 4 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 701 | -43 | Pre | 5 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 702 | -42 | Pre | 6 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 703 | -41 | Pre | 7 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 704 | -40 | Pre | 8 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 705 | -39 | Pre | 9 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 706 | -38 | Pre | 10 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 707 | -37 | Pre | 11 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 708 | -36 | Pre | 12 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 709 | -35 | Pre | 13 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 710 | -34 | Pre | 14 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 711 | -33 | Pre | 15 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 712 | -32 | Pre | 16 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 713 | -31 | Pre | 17 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 714 | -30 | Pre | 18 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 715 | -29 | Pre | 19 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 716 | -28 | Pre | 20 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 717 | -27 | Pre | 21 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 718 | -26 | Pre | 22 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 719 | -25 | Pre | 23 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 720 | -24 | Pre | 24 | -1 | 43099 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 721 | -23 | Pre | 1 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 722 | -22 | Pre | 2 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 723 | -21 | Pre | 3 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 724 | -20 | Pre | 4 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 725 | -19 | Pre | 5 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 726 | -18 | Pre | 6 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 727 | -17 | Pre | 7 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 728 | -16 | Pre | 8 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 729 | -15 | Pre | 9 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 730 | -14 | Pre | 10 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 731 | -13 | Pre | 11 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 732 | -12 | Pre | 12 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 733 | -11 | Pre | 13 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 734 | -10 | Pre | 14 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 735 | -9 | Pre | 15 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 736 | -8 | Pre | 16 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 737 | -7 | Pre | 17 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 738 | -6 | Pre | 18 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 739 | -5 | Pre | 19 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 740 | -4 | Pre | 20 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 741 | -3 | Pre | 21 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 742 | -2 | Pre | 22 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 743 | -1 | Pre | 23 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 744 | 0 | Pre | 24 | 0 | 43100 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 745 | 1 | 1 | 1 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 746 | 2 | 1 | 2 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 747 | 3 | 1 | 3 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 748 | 4 | 1 | 4 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 749 | 5 | 1 | 5 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 750 | 6 | 1 | 6 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 751 | 7 | 1 | 7 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 752 | 8 | 1 | 8 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 753 | 9 | 1 | 9 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 754 | 10 | 1 | 10 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 755 | 11 | 1 | 11 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 756 | 12 | 1 | 12 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 757 | 13 | 1 | 13 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 758 | 14 | 1 | 14 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 759 | 15 | 1 | 15 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 760 | 16 | 1 | 16 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 761 | 17 | 1 | 17 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 762 | 18 | 1 | 18 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 763 | 19 | 1 | 19 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 764 | 20 | 1 | 20 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 765 | 21 | 1 | 21 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 766 | 22 | 1 | 22 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 767 | 23 | 1 | 23 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 768 | 24 | 1 | 24 | 1 | 43101 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 769 | 25 | 1 | 1 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 770 | 26 | 1 | 2 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 771 | 27 | 1 | 3 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 772 | 28 | 1 | 4 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 773 | 29 | 1 | 5 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 774 | 30 | 1 | 6 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 775 | 31 | 1 | 7 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 776 | 32 | 1 | 8 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 777 | 33 | 1 | 9 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 778 | 34 | 1 | 10 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 779 | 35 | 1 | 11 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 780 | 36 | 1 | 12 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 781 | 37 | 1 | 13 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 782 | 38 | 1 | 14 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 783 | 39 | 1 | 15 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 784 | 40 | 1 | 16 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 785 | 41 | 1 | 17 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 786 | 42 | 1 | 18 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 787 | 43 | 1 | 19 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 788 | 44 | 1 | 20 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 789 | 45 | 1 | 21 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 790 | 46 | 1 | 22 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 791 | 47 | 1 | 23 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 792 | 48 | 1 | 24 | 2 | 43102 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 793 | 49 | 1 | 1 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 794 | 50 | 1 | 2 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 795 | 51 | 1 | 3 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 796 | 52 | 1 | 4 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 797 | 53 | 1 | 5 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 798 | 54 | 1 | 6 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 799 | 55 | 1 | 7 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 800 | 56 | 1 | 8 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 801 | 57 | 1 | 9 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 802 | 58 | 1 | 10 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 803 | 59 | 1 | 11 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 804 | 60 | 1 | 12 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 805 | 61 | 1 | 13 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 806 | 62 | 1 | 14 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 807 | 63 | 1 | 15 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 808 | 64 | 1 | 16 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 809 | 65 | 1 | 17 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 810 | 66 | 1 | 18 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 811 | 67 | 1 | 19 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 812 | 68 | 1 | 20 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 813 | 69 | 1 | 21 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 814 | 70 | 1 | 22 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 815 | 71 | 1 | 23 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 816 | 72 | 1 | 24 | 3 | 43103 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 817 | 73 | 1 | 1 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 818 | 74 | 1 | 2 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 819 | 75 | 1 | 3 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 820 | 76 | 1 | 4 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 821 | 77 | 1 | 5 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 822 | 78 | 1 | 6 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 823 | 79 | 1 | 7 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 824 | 80 | 1 | 8 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 825 | 81 | 1 | 9 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 826 | 82 | 1 | 10 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 827 | 83 | 1 | 11 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 828 | 84 | 1 | 12 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 829 | 85 | 1 | 13 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 830 | 86 | 1 | 14 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 831 | 87 | 1 | 15 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 832 | 88 | 1 | 16 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 833 | 89 | 1 | 17 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 834 | 90 | 1 | 18 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 835 | 91 | 1 | 19 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 836 | 92 | 1 | 20 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 837 | 93 | 1 | 21 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 838 | 94 | 1 | 22 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 839 | 95 | 1 | 23 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 840 | 96 | 1 | 24 | 4 | 43104 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 841 | 97 | 1 | 1 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 842 | 98 | 1 | 2 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 843 | 99 | 1 | 3 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 844 | 100 | 1 | 4 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 845 | 101 | 1 | 5 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 846 | 102 | 1 | 6 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 847 | 103 | 1 | 7 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 848 | 104 | 1 | 8 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 849 | 105 | 1 | 9 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 850 | 106 | 1 | 10 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 851 | 107 | 1 | 11 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 852 | 108 | 1 | 12 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 853 | 109 | 1 | 13 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 854 | 110 | 1 | 14 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 855 | 111 | 1 | 15 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 856 | 112 | 1 | 16 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 857 | 113 | 1 | 17 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 858 | 114 | 1 | 18 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 859 | 115 | 1 | 19 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 860 | 116 | 1 | 20 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 861 | 117 | 1 | 21 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 862 | 118 | 1 | 22 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 863 | 119 | 1 | 23 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 864 | 120 | 1 | 24 | 5 | 43105 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 865 | 121 | 1 | 1 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 866 | 122 | 1 | 2 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 867 | 123 | 1 | 3 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 868 | 124 | 1 | 4 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 869 | 125 | 1 | 5 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 870 | 126 | 1 | 6 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 871 | 127 | 1 | 7 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 872 | 128 | 1 | 8 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 873 | 129 | 1 | 9 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 874 | 130 | 1 | 10 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 875 | 131 | 1 | 11 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 876 | 132 | 1 | 12 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 877 | 133 | 1 | 13 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 878 | 134 | 1 | 14 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 879 | 135 | 1 | 15 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 880 | 136 | 1 | 16 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 881 | 137 | 1 | 17 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 882 | 138 | 1 | 18 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 883 | 139 | 1 | 19 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 884 | 140 | 1 | 20 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 885 | 141 | 1 | 21 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 886 | 142 | 1 | 22 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 887 | 143 | 1 | 23 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 888 | 144 | 1 | 24 | 6 | 43106 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 889 | 145 | 1 | 1 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 890 | 146 | 1 | 2 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 891 | 147 | 1 | 3 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 892 | 148 | 1 | 4 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 893 | 149 | 1 | 5 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 894 | 150 | 1 | 6 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 895 | 151 | 1 | 7 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 896 | 152 | 1 | 8 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 897 | 153 | 1 | 9 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 898 | 154 | 1 | 10 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 899 | 155 | 1 | 11 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 900 | 156 | 1 | 12 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 901 | 157 | 1 | 13 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 902 | 158 | 1 | 14 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 903 | 159 | 1 | 15 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 904 | 160 | 1 | 16 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 905 | 161 | 1 | 17 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 906 | 162 | 1 | 18 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 907 | 163 | 1 | 19 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 908 | 164 | 1 | 20 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 909 | 165 | 1 | 21 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 910 | 166 | 1 | 22 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 911 | 167 | 1 | 23 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 912 | 168 | 1 | 24 | 7 | 43107 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 913 | 169 | 1 | 1 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 914 | 170 | 1 | 2 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 915 | 171 | 1 | 3 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 916 | 172 | 1 | 4 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 917 | 173 | 1 | 5 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 918 | 174 | 1 | 6 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 919 | 175 | 1 | 7 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 920 | 176 | 1 | 8 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 921 | 177 | 1 | 9 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 922 | 178 | 1 | 10 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 923 | 179 | 1 | 11 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 924 | 180 | 1 | 12 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 925 | 181 | 1 | 13 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 926 | 182 | 1 | 14 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 927 | 183 | 1 | 15 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 928 | 184 | 1 | 16 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 929 | 185 | 1 | 17 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 930 | 186 | 1 | 18 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 931 | 187 | 1 | 19 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 932 | 188 | 1 | 20 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 933 | 189 | 1 | 21 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 934 | 190 | 1 | 22 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 935 | 191 | 1 | 23 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 936 | 192 | 1 | 24 | 8 | 43108 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 937 | 193 | 1 | 1 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 938 | 194 | 1 | 2 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 939 | 195 | 1 | 3 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 940 | 196 | 1 | 4 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 941 | 197 | 1 | 5 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 942 | 198 | 1 | 6 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 943 | 199 | 1 | 7 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 944 | 200 | 1 | 8 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 945 | 201 | 1 | 9 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 946 | 202 | 1 | 10 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 947 | 203 | 1 | 11 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 948 | 204 | 1 | 12 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 949 | 205 | 1 | 13 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 950 | 206 | 1 | 14 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 951 | 207 | 1 | 15 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 952 | 208 | 1 | 16 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 953 | 209 | 1 | 17 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 954 | 210 | 1 | 18 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 955 | 211 | 1 | 19 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 956 | 212 | 1 | 20 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 957 | 213 | 1 | 21 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 958 | 214 | 1 | 22 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 959 | 215 | 1 | 23 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 960 | 216 | 1 | 24 | 9 | 43109 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 961 | 217 | 1 | 1 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 962 | 218 | 1 | 2 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 963 | 219 | 1 | 3 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 964 | 220 | 1 | 4 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 965 | 221 | 1 | 5 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 966 | 222 | 1 | 6 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 967 | 223 | 1 | 7 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 968 | 224 | 1 | 8 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 969 | 225 | 1 | 9 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 970 | 226 | 1 | 10 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 971 | 227 | 1 | 11 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 972 | 228 | 1 | 12 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 973 | 229 | 1 | 13 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 974 | 230 | 1 | 14 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 975 | 231 | 1 | 15 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 976 | 232 | 1 | 16 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 977 | 233 | 1 | 17 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 978 | 234 | 1 | 18 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 979 | 235 | 1 | 19 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 980 | 236 | 1 | 20 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 981 | 237 | 1 | 21 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 982 | 238 | 1 | 22 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 983 | 239 | 1 | 23 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 984 | 240 | 1 | 24 | 10 | 43110 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 985 | 241 | 1 | 1 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 986 | 242 | 1 | 2 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 987 | 243 | 1 | 3 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 988 | 244 | 1 | 4 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 989 | 245 | 1 | 5 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 990 | 246 | 1 | 6 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 991 | 247 | 1 | 7 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 992 | 248 | 1 | 8 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 993 | 249 | 1 | 9 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 994 | 250 | 1 | 10 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 995 | 251 | 1 | 11 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 996 | 252 | 1 | 12 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 997 | 253 | 1 | 13 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 998 | 254 | 1 | 14 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 999 | 255 | 1 | 15 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1000 | 256 | 1 | 16 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1001 | 257 | 1 | 17 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1002 | 258 | 1 | 18 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1003 | 259 | 1 | 19 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1004 | 260 | 1 | 20 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1005 | 261 | 1 | 21 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1006 | 262 | 1 | 22 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1007 | 263 | 1 | 23 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1008 | 264 | 1 | 24 | 11 | 43111 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1009 | 265 | 1 | 1 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1010 | 266 | 1 | 2 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1011 | 267 | 1 | 3 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1012 | 268 | 1 | 4 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1013 | 269 | 1 | 5 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1014 | 270 | 1 | 6 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1015 | 271 | 1 | 7 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1016 | 272 | 1 | 8 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1017 | 273 | 1 | 9 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1018 | 274 | 1 | 10 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1019 | 275 | 1 | 11 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1020 | 276 | 1 | 12 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1021 | 277 | 1 | 13 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1022 | 278 | 1 | 14 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1023 | 279 | 1 | 15 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1024 | 280 | 1 | 16 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1025 | 281 | 1 | 17 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1026 | 282 | 1 | 18 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1027 | 283 | 1 | 19 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1028 | 284 | 1 | 20 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1029 | 285 | 1 | 21 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1030 | 286 | 1 | 22 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1031 | 287 | 1 | 23 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1032 | 288 | 1 | 24 | 12 | 43112 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1033 | 289 | 1 | 1 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1034 | 290 | 1 | 2 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1035 | 291 | 1 | 3 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1036 | 292 | 1 | 4 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1037 | 293 | 1 | 5 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1038 | 294 | 1 | 6 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1039 | 295 | 1 | 7 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1040 | 296 | 1 | 8 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1041 | 297 | 1 | 9 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1042 | 298 | 1 | 10 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1043 | 299 | 1 | 11 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1044 | 300 | 1 | 12 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1045 | 301 | 1 | 13 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1046 | 302 | 1 | 14 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1047 | 303 | 1 | 15 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1048 | 304 | 1 | 16 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1049 | 305 | 1 | 17 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1050 | 306 | 1 | 18 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1051 | 307 | 1 | 19 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1052 | 308 | 1 | 20 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1053 | 309 | 1 | 21 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1054 | 310 | 1 | 22 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1055 | 311 | 1 | 23 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1056 | 312 | 1 | 24 | 13 | 43113 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1057 | 313 | 1 | 1 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1058 | 314 | 1 | 2 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1059 | 315 | 1 | 3 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1060 | 316 | 1 | 4 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1061 | 317 | 1 | 5 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1062 | 318 | 1 | 6 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1063 | 319 | 1 | 7 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1064 | 320 | 1 | 8 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1065 | 321 | 1 | 9 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1066 | 322 | 1 | 10 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1067 | 323 | 1 | 11 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1068 | 324 | 1 | 12 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1069 | 325 | 1 | 13 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1070 | 326 | 1 | 14 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1071 | 327 | 1 | 15 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1072 | 328 | 1 | 16 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1073 | 329 | 1 | 17 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1074 | 330 | 1 | 18 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1075 | 331 | 1 | 19 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1076 | 332 | 1 | 20 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1077 | 333 | 1 | 21 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1078 | 334 | 1 | 22 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1079 | 335 | 1 | 23 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1080 | 336 | 1 | 24 | 14 | 43114 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1081 | 337 | 1 | 1 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1082 | 338 | 1 | 2 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1083 | 339 | 1 | 3 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1084 | 340 | 1 | 4 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1085 | 341 | 1 | 5 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1086 | 342 | 1 | 6 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1087 | 343 | 1 | 7 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1088 | 344 | 1 | 8 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1089 | 345 | 1 | 9 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1090 | 346 | 1 | 10 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1091 | 347 | 1 | 11 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1092 | 348 | 1 | 12 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1093 | 349 | 1 | 13 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1094 | 350 | 1 | 14 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1095 | 351 | 1 | 15 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1096 | 352 | 1 | 16 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1097 | 353 | 1 | 17 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1098 | 354 | 1 | 18 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1099 | 355 | 1 | 19 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1100 | 356 | 1 | 20 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1101 | 357 | 1 | 21 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1102 | 358 | 1 | 22 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1103 | 359 | 1 | 23 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1104 | 360 | 1 | 24 | 15 | 43115 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1105 | 361 | 1 | 1 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1106 | 362 | 1 | 2 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1107 | 363 | 1 | 3 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1108 | 364 | 1 | 4 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1109 | 365 | 1 | 5 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1110 | 366 | 1 | 6 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1111 | 367 | 1 | 7 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1112 | 368 | 1 | 8 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1113 | 369 | 1 | 9 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1114 | 370 | 1 | 10 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1115 | 371 | 1 | 11 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1116 | 372 | 1 | 12 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1117 | 373 | 1 | 13 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1118 | 374 | 1 | 14 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1119 | 375 | 1 | 15 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1120 | 376 | 1 | 16 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1121 | 377 | 1 | 17 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1122 | 378 | 1 | 18 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1123 | 379 | 1 | 19 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1124 | 380 | 1 | 20 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1125 | 381 | 1 | 21 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1126 | 382 | 1 | 22 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1127 | 383 | 1 | 23 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1128 | 384 | 1 | 24 | 16 | 43116 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1129 | 385 | 1 | 1 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1130 | 386 | 1 | 2 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1131 | 387 | 1 | 3 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1132 | 388 | 1 | 4 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1133 | 389 | 1 | 5 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1134 | 390 | 1 | 6 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1135 | 391 | 1 | 7 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1136 | 392 | 1 | 8 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1137 | 393 | 1 | 9 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1138 | 394 | 1 | 10 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1139 | 395 | 1 | 11 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1140 | 396 | 1 | 12 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1141 | 397 | 1 | 13 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1142 | 398 | 1 | 14 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1143 | 399 | 1 | 15 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1144 | 400 | 1 | 16 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1145 | 401 | 1 | 17 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1146 | 402 | 1 | 18 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1147 | 403 | 1 | 19 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1148 | 404 | 1 | 20 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1149 | 405 | 1 | 21 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1150 | 406 | 1 | 22 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1151 | 407 | 1 | 23 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1152 | 408 | 1 | 24 | 17 | 43117 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1153 | 409 | 1 | 1 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1154 | 410 | 1 | 2 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1155 | 411 | 1 | 3 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1156 | 412 | 1 | 4 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1157 | 413 | 1 | 5 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1158 | 414 | 1 | 6 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1159 | 415 | 1 | 7 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1160 | 416 | 1 | 8 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1161 | 417 | 1 | 9 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1162 | 418 | 1 | 10 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1163 | 419 | 1 | 11 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1164 | 420 | 1 | 12 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1165 | 421 | 1 | 13 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1166 | 422 | 1 | 14 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1167 | 423 | 1 | 15 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1168 | 424 | 1 | 16 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1169 | 425 | 1 | 17 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1170 | 426 | 1 | 18 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1171 | 427 | 1 | 19 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1172 | 428 | 1 | 20 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1173 | 429 | 1 | 21 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1174 | 430 | 1 | 22 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1175 | 431 | 1 | 23 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1176 | 432 | 1 | 24 | 18 | 43118 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1177 | 433 | 1 | 1 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1178 | 434 | 1 | 2 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1179 | 435 | 1 | 3 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1180 | 436 | 1 | 4 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1181 | 437 | 1 | 5 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1182 | 438 | 1 | 6 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1183 | 439 | 1 | 7 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1184 | 440 | 1 | 8 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1185 | 441 | 1 | 9 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1186 | 442 | 1 | 10 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1187 | 443 | 1 | 11 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1188 | 444 | 1 | 12 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1189 | 445 | 1 | 13 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1190 | 446 | 1 | 14 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1191 | 447 | 1 | 15 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1192 | 448 | 1 | 16 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1193 | 449 | 1 | 17 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1194 | 450 | 1 | 18 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1195 | 451 | 1 | 19 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1196 | 452 | 1 | 20 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1197 | 453 | 1 | 21 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1198 | 454 | 1 | 22 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1199 | 455 | 1 | 23 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1200 | 456 | 1 | 24 | 19 | 43119 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1201 | 457 | 1 | 1 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1202 | 458 | 1 | 2 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1203 | 459 | 1 | 3 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1204 | 460 | 1 | 4 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1205 | 461 | 1 | 5 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1206 | 462 | 1 | 6 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1207 | 463 | 1 | 7 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1208 | 464 | 1 | 8 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1209 | 465 | 1 | 9 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1210 | 466 | 1 | 10 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1211 | 467 | 1 | 11 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1212 | 468 | 1 | 12 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1213 | 469 | 1 | 13 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1214 | 470 | 1 | 14 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1215 | 471 | 1 | 15 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1216 | 472 | 1 | 16 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1217 | 473 | 1 | 17 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1218 | 474 | 1 | 18 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1219 | 475 | 1 | 19 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1220 | 476 | 1 | 20 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1221 | 477 | 1 | 21 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1222 | 478 | 1 | 22 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1223 | 479 | 1 | 23 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1224 | 480 | 1 | 24 | 20 | 43120 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1225 | 481 | 1 | 1 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1226 | 482 | 1 | 2 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1227 | 483 | 1 | 3 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1228 | 484 | 1 | 4 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1229 | 485 | 1 | 5 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1230 | 486 | 1 | 6 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1231 | 487 | 1 | 7 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1232 | 488 | 1 | 8 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1233 | 489 | 1 | 9 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1234 | 490 | 1 | 10 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1235 | 491 | 1 | 11 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1236 | 492 | 1 | 12 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1237 | 493 | 1 | 13 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1238 | 494 | 1 | 14 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1239 | 495 | 1 | 15 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1240 | 496 | 1 | 16 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1241 | 497 | 1 | 17 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1242 | 498 | 1 | 18 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1243 | 499 | 1 | 19 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1244 | 500 | 1 | 20 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1245 | 501 | 1 | 21 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1246 | 502 | 1 | 22 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1247 | 503 | 1 | 23 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1248 | 504 | 1 | 24 | 21 | 43121 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1249 | 505 | 1 | 1 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1250 | 506 | 1 | 2 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1251 | 507 | 1 | 3 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1252 | 508 | 1 | 4 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1253 | 509 | 1 | 5 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1254 | 510 | 1 | 6 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1255 | 511 | 1 | 7 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1256 | 512 | 1 | 8 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1257 | 513 | 1 | 9 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1258 | 514 | 1 | 10 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1259 | 515 | 1 | 11 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1260 | 516 | 1 | 12 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1261 | 517 | 1 | 13 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1262 | 518 | 1 | 14 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1263 | 519 | 1 | 15 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1264 | 520 | 1 | 16 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1265 | 521 | 1 | 17 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1266 | 522 | 1 | 18 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1267 | 523 | 1 | 19 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1268 | 524 | 1 | 20 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1269 | 525 | 1 | 21 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1270 | 526 | 1 | 22 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1271 | 527 | 1 | 23 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1272 | 528 | 1 | 24 | 22 | 43122 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1273 | 529 | 1 | 1 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1274 | 530 | 1 | 2 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1275 | 531 | 1 | 3 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1276 | 532 | 1 | 4 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1277 | 533 | 1 | 5 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1278 | 534 | 1 | 6 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1279 | 535 | 1 | 7 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1280 | 536 | 1 | 8 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1281 | 537 | 1 | 9 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1282 | 538 | 1 | 10 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1283 | 539 | 1 | 11 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1284 | 540 | 1 | 12 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1285 | 541 | 1 | 13 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1286 | 542 | 1 | 14 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1287 | 543 | 1 | 15 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1288 | 544 | 1 | 16 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1289 | 545 | 1 | 17 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1290 | 546 | 1 | 18 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1291 | 547 | 1 | 19 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1292 | 548 | 1 | 20 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1293 | 549 | 1 | 21 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1294 | 550 | 1 | 22 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1295 | 551 | 1 | 23 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1296 | 552 | 1 | 24 | 23 | 43123 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1297 | 553 | 1 | 1 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1298 | 554 | 1 | 2 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1299 | 555 | 1 | 3 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1300 | 556 | 1 | 4 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1301 | 557 | 1 | 5 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1302 | 558 | 1 | 6 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1303 | 559 | 1 | 7 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1304 | 560 | 1 | 8 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1305 | 561 | 1 | 9 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1306 | 562 | 1 | 10 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1307 | 563 | 1 | 11 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1308 | 564 | 1 | 12 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1309 | 565 | 1 | 13 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1310 | 566 | 1 | 14 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1311 | 567 | 1 | 15 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1312 | 568 | 1 | 16 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1313 | 569 | 1 | 17 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1314 | 570 | 1 | 18 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1315 | 571 | 1 | 19 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1316 | 572 | 1 | 20 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1317 | 573 | 1 | 21 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1318 | 574 | 1 | 22 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1319 | 575 | 1 | 23 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1320 | 576 | 1 | 24 | 24 | 43124 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1321 | 577 | 1 | 1 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1322 | 578 | 1 | 2 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1323 | 579 | 1 | 3 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1324 | 580 | 1 | 4 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1325 | 581 | 1 | 5 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1326 | 582 | 1 | 6 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1327 | 583 | 1 | 7 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1328 | 584 | 1 | 8 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1329 | 585 | 1 | 9 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1330 | 586 | 1 | 10 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1331 | 587 | 1 | 11 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1332 | 588 | 1 | 12 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1333 | 589 | 1 | 13 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1334 | 590 | 1 | 14 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1335 | 591 | 1 | 15 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1336 | 592 | 1 | 16 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1337 | 593 | 1 | 17 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1338 | 594 | 1 | 18 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1339 | 595 | 1 | 19 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1340 | 596 | 1 | 20 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1341 | 597 | 1 | 21 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1342 | 598 | 1 | 22 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1343 | 599 | 1 | 23 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1344 | 600 | 1 | 24 | 25 | 43125 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1345 | 601 | 1 | 1 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1346 | 602 | 1 | 2 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1347 | 603 | 1 | 3 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1348 | 604 | 1 | 4 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1349 | 605 | 1 | 5 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1350 | 606 | 1 | 6 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1351 | 607 | 1 | 7 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1352 | 608 | 1 | 8 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1353 | 609 | 1 | 9 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1354 | 610 | 1 | 10 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1355 | 611 | 1 | 11 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1356 | 612 | 1 | 12 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1357 | 613 | 1 | 13 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1358 | 614 | 1 | 14 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1359 | 615 | 1 | 15 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1360 | 616 | 1 | 16 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1361 | 617 | 1 | 17 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1362 | 618 | 1 | 18 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1363 | 619 | 1 | 19 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1364 | 620 | 1 | 20 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1365 | 621 | 1 | 21 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1366 | 622 | 1 | 22 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1367 | 623 | 1 | 23 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1368 | 624 | 1 | 24 | 26 | 43126 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1369 | 625 | 1 | 1 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1370 | 626 | 1 | 2 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1371 | 627 | 1 | 3 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1372 | 628 | 1 | 4 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1373 | 629 | 1 | 5 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1374 | 630 | 1 | 6 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1375 | 631 | 1 | 7 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1376 | 632 | 1 | 8 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1377 | 633 | 1 | 9 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1378 | 634 | 1 | 10 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1379 | 635 | 1 | 11 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1380 | 636 | 1 | 12 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1381 | 637 | 1 | 13 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1382 | 638 | 1 | 14 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1383 | 639 | 1 | 15 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1384 | 640 | 1 | 16 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1385 | 641 | 1 | 17 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1386 | 642 | 1 | 18 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1387 | 643 | 1 | 19 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1388 | 644 | 1 | 20 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1389 | 645 | 1 | 21 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1390 | 646 | 1 | 22 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1391 | 647 | 1 | 23 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1392 | 648 | 1 | 24 | 27 | 43127 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1393 | 649 | 1 | 1 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1394 | 650 | 1 | 2 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1395 | 651 | 1 | 3 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1396 | 652 | 1 | 4 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1397 | 653 | 1 | 5 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1398 | 654 | 1 | 6 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1399 | 655 | 1 | 7 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1400 | 656 | 1 | 8 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1401 | 657 | 1 | 9 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1402 | 658 | 1 | 10 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1403 | 659 | 1 | 11 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1404 | 660 | 1 | 12 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1405 | 661 | 1 | 13 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1406 | 662 | 1 | 14 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1407 | 663 | 1 | 15 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1408 | 664 | 1 | 16 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1409 | 665 | 1 | 17 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1410 | 666 | 1 | 18 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1411 | 667 | 1 | 19 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1412 | 668 | 1 | 20 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1413 | 669 | 1 | 21 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1414 | 670 | 1 | 22 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1415 | 671 | 1 | 23 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1416 | 672 | 1 | 24 | 28 | 43128 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1417 | 673 | 1 | 1 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1418 | 674 | 1 | 2 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1419 | 675 | 1 | 3 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1420 | 676 | 1 | 4 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1421 | 677 | 1 | 5 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1422 | 678 | 1 | 6 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1423 | 679 | 1 | 7 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1424 | 680 | 1 | 8 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1425 | 681 | 1 | 9 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1426 | 682 | 1 | 10 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1427 | 683 | 1 | 11 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1428 | 684 | 1 | 12 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1429 | 685 | 1 | 13 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1430 | 686 | 1 | 14 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1431 | 687 | 1 | 15 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1432 | 688 | 1 | 16 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1433 | 689 | 1 | 17 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1434 | 690 | 1 | 18 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1435 | 691 | 1 | 19 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1436 | 692 | 1 | 20 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1437 | 693 | 1 | 21 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1438 | 694 | 1 | 22 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1439 | 695 | 1 | 23 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1440 | 696 | 1 | 24 | 29 | 43129 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1441 | 697 | 1 | 1 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1442 | 698 | 1 | 2 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1443 | 699 | 1 | 3 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1444 | 700 | 1 | 4 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1445 | 701 | 1 | 5 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1446 | 702 | 1 | 6 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1447 | 703 | 1 | 7 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1448 | 704 | 1 | 8 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1449 | 705 | 1 | 9 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1450 | 706 | 1 | 10 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1451 | 707 | 1 | 11 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1452 | 708 | 1 | 12 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1453 | 709 | 1 | 13 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1454 | 710 | 1 | 14 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1455 | 711 | 1 | 15 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1456 | 712 | 1 | 16 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1457 | 713 | 1 | 17 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1458 | 714 | 1 | 18 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1459 | 715 | 1 | 19 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1460 | 716 | 1 | 20 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1461 | 717 | 1 | 21 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1462 | 718 | 1 | 22 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1463 | 719 | 1 | 23 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1464 | 720 | 1 | 24 | 30 | 43130 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1465 | 721 | 1 | 1 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1466 | 722 | 1 | 2 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1467 | 723 | 1 | 3 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1468 | 724 | 1 | 4 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1469 | 725 | 1 | 5 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1470 | 726 | 1 | 6 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1471 | 727 | 1 | 7 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1472 | 728 | 1 | 8 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1473 | 729 | 1 | 9 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1474 | 730 | 1 | 10 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1475 | 731 | 1 | 11 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1476 | 732 | 1 | 12 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1477 | 733 | 1 | 13 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1478 | 734 | 1 | 14 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1479 | 735 | 1 | 15 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1480 | 736 | 1 | 16 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1481 | 737 | 1 | 17 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1482 | 738 | 1 | 18 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1483 | 739 | 1 | 19 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1484 | 740 | 1 | 20 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1485 | 741 | 1 | 21 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1486 | 742 | 1 | 22 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1487 | 743 | 1 | 23 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1488 | 744 | 1 | 24 | 31 | 43131 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1489 | 745 | 2 | 1 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1490 | 746 | 2 | 2 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1491 | 747 | 2 | 3 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1492 | 748 | 2 | 4 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1493 | 749 | 2 | 5 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1494 | 750 | 2 | 6 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1495 | 751 | 2 | 7 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1496 | 752 | 2 | 8 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1497 | 753 | 2 | 9 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1498 | 754 | 2 | 10 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1499 | 755 | 2 | 11 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1500 | 756 | 2 | 12 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1501 | 757 | 2 | 13 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1502 | 758 | 2 | 14 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1503 | 759 | 2 | 15 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1504 | 760 | 2 | 16 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1505 | 761 | 2 | 17 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1506 | 762 | 2 | 18 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1507 | 763 | 2 | 19 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1508 | 764 | 2 | 20 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1509 | 765 | 2 | 21 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1510 | 766 | 2 | 22 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1511 | 767 | 2 | 23 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1512 | 768 | 2 | 24 | 32 | 43132 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1513 | 769 | 2 | 1 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1514 | 770 | 2 | 2 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1515 | 771 | 2 | 3 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1516 | 772 | 2 | 4 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1517 | 773 | 2 | 5 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1518 | 774 | 2 | 6 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1519 | 775 | 2 | 7 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1520 | 776 | 2 | 8 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1521 | 777 | 2 | 9 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1522 | 778 | 2 | 10 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1523 | 779 | 2 | 11 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1524 | 780 | 2 | 12 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1525 | 781 | 2 | 13 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1526 | 782 | 2 | 14 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1527 | 783 | 2 | 15 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1528 | 784 | 2 | 16 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1529 | 785 | 2 | 17 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1530 | 786 | 2 | 18 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1531 | 787 | 2 | 19 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1532 | 788 | 2 | 20 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1533 | 789 | 2 | 21 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1534 | 790 | 2 | 22 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1535 | 791 | 2 | 23 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1536 | 792 | 2 | 24 | 33 | 43133 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1537 | 793 | 2 | 1 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1538 | 794 | 2 | 2 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1539 | 795 | 2 | 3 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1540 | 796 | 2 | 4 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1541 | 797 | 2 | 5 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1542 | 798 | 2 | 6 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1543 | 799 | 2 | 7 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1544 | 800 | 2 | 8 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1545 | 801 | 2 | 9 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1546 | 802 | 2 | 10 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1547 | 803 | 2 | 11 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1548 | 804 | 2 | 12 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1549 | 805 | 2 | 13 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1550 | 806 | 2 | 14 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1551 | 807 | 2 | 15 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1552 | 808 | 2 | 16 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1553 | 809 | 2 | 17 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1554 | 810 | 2 | 18 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1555 | 811 | 2 | 19 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1556 | 812 | 2 | 20 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1557 | 813 | 2 | 21 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1558 | 814 | 2 | 22 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1559 | 815 | 2 | 23 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1560 | 816 | 2 | 24 | 34 | 43134 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1561 | 817 | 2 | 1 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1562 | 818 | 2 | 2 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1563 | 819 | 2 | 3 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1564 | 820 | 2 | 4 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1565 | 821 | 2 | 5 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1566 | 822 | 2 | 6 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1567 | 823 | 2 | 7 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1568 | 824 | 2 | 8 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1569 | 825 | 2 | 9 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1570 | 826 | 2 | 10 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1571 | 827 | 2 | 11 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1572 | 828 | 2 | 12 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1573 | 829 | 2 | 13 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1574 | 830 | 2 | 14 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1575 | 831 | 2 | 15 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1576 | 832 | 2 | 16 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1577 | 833 | 2 | 17 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1578 | 834 | 2 | 18 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1579 | 835 | 2 | 19 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1580 | 836 | 2 | 20 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1581 | 837 | 2 | 21 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1582 | 838 | 2 | 22 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1583 | 839 | 2 | 23 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1584 | 840 | 2 | 24 | 35 | 43135 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1585 | 841 | 2 | 1 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1586 | 842 | 2 | 2 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1587 | 843 | 2 | 3 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1588 | 844 | 2 | 4 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1589 | 845 | 2 | 5 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1590 | 846 | 2 | 6 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1591 | 847 | 2 | 7 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1592 | 848 | 2 | 8 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1593 | 849 | 2 | 9 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1594 | 850 | 2 | 10 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1595 | 851 | 2 | 11 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1596 | 852 | 2 | 12 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1597 | 853 | 2 | 13 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1598 | 854 | 2 | 14 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1599 | 855 | 2 | 15 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1600 | 856 | 2 | 16 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1601 | 857 | 2 | 17 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1602 | 858 | 2 | 18 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1603 | 859 | 2 | 19 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1604 | 860 | 2 | 20 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1605 | 861 | 2 | 21 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1606 | 862 | 2 | 22 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1607 | 863 | 2 | 23 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1608 | 864 | 2 | 24 | 36 | 43136 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1609 | 865 | 2 | 1 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1610 | 866 | 2 | 2 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1611 | 867 | 2 | 3 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1612 | 868 | 2 | 4 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1613 | 869 | 2 | 5 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1614 | 870 | 2 | 6 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1615 | 871 | 2 | 7 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1616 | 872 | 2 | 8 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1617 | 873 | 2 | 9 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1618 | 874 | 2 | 10 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1619 | 875 | 2 | 11 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1620 | 876 | 2 | 12 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1621 | 877 | 2 | 13 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1622 | 878 | 2 | 14 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1623 | 879 | 2 | 15 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1624 | 880 | 2 | 16 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1625 | 881 | 2 | 17 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1626 | 882 | 2 | 18 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1627 | 883 | 2 | 19 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1628 | 884 | 2 | 20 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1629 | 885 | 2 | 21 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1630 | 886 | 2 | 22 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1631 | 887 | 2 | 23 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1632 | 888 | 2 | 24 | 37 | 43137 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1633 | 889 | 2 | 1 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1634 | 890 | 2 | 2 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1635 | 891 | 2 | 3 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1636 | 892 | 2 | 4 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1637 | 893 | 2 | 5 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1638 | 894 | 2 | 6 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1639 | 895 | 2 | 7 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1640 | 896 | 2 | 8 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1641 | 897 | 2 | 9 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1642 | 898 | 2 | 10 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1643 | 899 | 2 | 11 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1644 | 900 | 2 | 12 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1645 | 901 | 2 | 13 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1646 | 902 | 2 | 14 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1647 | 903 | 2 | 15 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1648 | 904 | 2 | 16 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1649 | 905 | 2 | 17 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1650 | 906 | 2 | 18 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1651 | 907 | 2 | 19 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1652 | 908 | 2 | 20 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1653 | 909 | 2 | 21 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1654 | 910 | 2 | 22 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1655 | 911 | 2 | 23 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1656 | 912 | 2 | 24 | 38 | 43138 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1657 | 913 | 2 | 1 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1658 | 914 | 2 | 2 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1659 | 915 | 2 | 3 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1660 | 916 | 2 | 4 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1661 | 917 | 2 | 5 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1662 | 918 | 2 | 6 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1663 | 919 | 2 | 7 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1664 | 920 | 2 | 8 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1665 | 921 | 2 | 9 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1666 | 922 | 2 | 10 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1667 | 923 | 2 | 11 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1668 | 924 | 2 | 12 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1669 | 925 | 2 | 13 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1670 | 926 | 2 | 14 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1671 | 927 | 2 | 15 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1672 | 928 | 2 | 16 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1673 | 929 | 2 | 17 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1674 | 930 | 2 | 18 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1675 | 931 | 2 | 19 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1676 | 932 | 2 | 20 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1677 | 933 | 2 | 21 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1678 | 934 | 2 | 22 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1679 | 935 | 2 | 23 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1680 | 936 | 2 | 24 | 39 | 43139 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1681 | 937 | 2 | 1 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1682 | 938 | 2 | 2 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1683 | 939 | 2 | 3 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1684 | 940 | 2 | 4 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1685 | 941 | 2 | 5 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1686 | 942 | 2 | 6 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1687 | 943 | 2 | 7 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1688 | 944 | 2 | 8 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1689 | 945 | 2 | 9 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1690 | 946 | 2 | 10 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1691 | 947 | 2 | 11 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1692 | 948 | 2 | 12 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1693 | 949 | 2 | 13 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1694 | 950 | 2 | 14 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1695 | 951 | 2 | 15 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1696 | 952 | 2 | 16 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1697 | 953 | 2 | 17 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1698 | 954 | 2 | 18 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1699 | 955 | 2 | 19 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1700 | 956 | 2 | 20 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1701 | 957 | 2 | 21 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1702 | 958 | 2 | 22 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1703 | 959 | 2 | 23 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1704 | 960 | 2 | 24 | 40 | 43140 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1705 | 961 | 2 | 1 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1706 | 962 | 2 | 2 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1707 | 963 | 2 | 3 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1708 | 964 | 2 | 4 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1709 | 965 | 2 | 5 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1710 | 966 | 2 | 6 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1711 | 967 | 2 | 7 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1712 | 968 | 2 | 8 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1713 | 969 | 2 | 9 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1714 | 970 | 2 | 10 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1715 | 971 | 2 | 11 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1716 | 972 | 2 | 12 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1717 | 973 | 2 | 13 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1718 | 974 | 2 | 14 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1719 | 975 | 2 | 15 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1720 | 976 | 2 | 16 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1721 | 977 | 2 | 17 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1722 | 978 | 2 | 18 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1723 | 979 | 2 | 19 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1724 | 980 | 2 | 20 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1725 | 981 | 2 | 21 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1726 | 982 | 2 | 22 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1727 | 983 | 2 | 23 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1728 | 984 | 2 | 24 | 41 | 43141 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1729 | 985 | 2 | 1 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1730 | 986 | 2 | 2 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1731 | 987 | 2 | 3 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1732 | 988 | 2 | 4 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1733 | 989 | 2 | 5 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1734 | 990 | 2 | 6 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1735 | 991 | 2 | 7 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1736 | 992 | 2 | 8 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1737 | 993 | 2 | 9 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1738 | 994 | 2 | 10 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1739 | 995 | 2 | 11 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1740 | 996 | 2 | 12 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1741 | 997 | 2 | 13 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1742 | 998 | 2 | 14 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1743 | 999 | 2 | 15 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1744 | 1000 | 2 | 16 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1745 | 1001 | 2 | 17 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1746 | 1002 | 2 | 18 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1747 | 1003 | 2 | 19 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1748 | 1004 | 2 | 20 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1749 | 1005 | 2 | 21 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1750 | 1006 | 2 | 22 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1751 | 1007 | 2 | 23 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1752 | 1008 | 2 | 24 | 42 | 43142 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1753 | 1009 | 2 | 1 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1754 | 1010 | 2 | 2 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1755 | 1011 | 2 | 3 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1756 | 1012 | 2 | 4 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1757 | 1013 | 2 | 5 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1758 | 1014 | 2 | 6 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1759 | 1015 | 2 | 7 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1760 | 1016 | 2 | 8 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1761 | 1017 | 2 | 9 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1762 | 1018 | 2 | 10 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1763 | 1019 | 2 | 11 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1764 | 1020 | 2 | 12 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1765 | 1021 | 2 | 13 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1766 | 1022 | 2 | 14 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1767 | 1023 | 2 | 15 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1768 | 1024 | 2 | 16 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1769 | 1025 | 2 | 17 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1770 | 1026 | 2 | 18 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1771 | 1027 | 2 | 19 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1772 | 1028 | 2 | 20 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1773 | 1029 | 2 | 21 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1774 | 1030 | 2 | 22 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1775 | 1031 | 2 | 23 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1776 | 1032 | 2 | 24 | 43 | 43143 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1777 | 1033 | 2 | 1 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1778 | 1034 | 2 | 2 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1779 | 1035 | 2 | 3 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1780 | 1036 | 2 | 4 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1781 | 1037 | 2 | 5 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1782 | 1038 | 2 | 6 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1783 | 1039 | 2 | 7 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1784 | 1040 | 2 | 8 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1785 | 1041 | 2 | 9 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1786 | 1042 | 2 | 10 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1787 | 1043 | 2 | 11 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1788 | 1044 | 2 | 12 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1789 | 1045 | 2 | 13 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1790 | 1046 | 2 | 14 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1791 | 1047 | 2 | 15 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1792 | 1048 | 2 | 16 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1793 | 1049 | 2 | 17 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1794 | 1050 | 2 | 18 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1795 | 1051 | 2 | 19 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1796 | 1052 | 2 | 20 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1797 | 1053 | 2 | 21 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1798 | 1054 | 2 | 22 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1799 | 1055 | 2 | 23 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1800 | 1056 | 2 | 24 | 44 | 43144 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1801 | 1057 | 2 | 1 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1802 | 1058 | 2 | 2 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1803 | 1059 | 2 | 3 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1804 | 1060 | 2 | 4 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1805 | 1061 | 2 | 5 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1806 | 1062 | 2 | 6 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1807 | 1063 | 2 | 7 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1808 | 1064 | 2 | 8 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1809 | 1065 | 2 | 9 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1810 | 1066 | 2 | 10 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1811 | 1067 | 2 | 11 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1812 | 1068 | 2 | 12 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1813 | 1069 | 2 | 13 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1814 | 1070 | 2 | 14 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1815 | 1071 | 2 | 15 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1816 | 1072 | 2 | 16 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1817 | 1073 | 2 | 17 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1818 | 1074 | 2 | 18 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1819 | 1075 | 2 | 19 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1820 | 1076 | 2 | 20 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1821 | 1077 | 2 | 21 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1822 | 1078 | 2 | 22 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1823 | 1079 | 2 | 23 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1824 | 1080 | 2 | 24 | 45 | 43145 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1825 | 1081 | 2 | 1 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1826 | 1082 | 2 | 2 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1827 | 1083 | 2 | 3 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1828 | 1084 | 2 | 4 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1829 | 1085 | 2 | 5 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1830 | 1086 | 2 | 6 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1831 | 1087 | 2 | 7 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1832 | 1088 | 2 | 8 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1833 | 1089 | 2 | 9 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1834 | 1090 | 2 | 10 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1835 | 1091 | 2 | 11 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1836 | 1092 | 2 | 12 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1837 | 1093 | 2 | 13 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1838 | 1094 | 2 | 14 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1839 | 1095 | 2 | 15 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1840 | 1096 | 2 | 16 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1841 | 1097 | 2 | 17 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1842 | 1098 | 2 | 18 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1843 | 1099 | 2 | 19 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1844 | 1100 | 2 | 20 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1845 | 1101 | 2 | 21 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1846 | 1102 | 2 | 22 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1847 | 1103 | 2 | 23 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1848 | 1104 | 2 | 24 | 46 | 43146 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1849 | 1105 | 2 | 1 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1850 | 1106 | 2 | 2 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1851 | 1107 | 2 | 3 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1852 | 1108 | 2 | 4 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1853 | 1109 | 2 | 5 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1854 | 1110 | 2 | 6 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1855 | 1111 | 2 | 7 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1856 | 1112 | 2 | 8 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1857 | 1113 | 2 | 9 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1858 | 1114 | 2 | 10 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1859 | 1115 | 2 | 11 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1860 | 1116 | 2 | 12 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1861 | 1117 | 2 | 13 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1862 | 1118 | 2 | 14 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1863 | 1119 | 2 | 15 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1864 | 1120 | 2 | 16 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1865 | 1121 | 2 | 17 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1866 | 1122 | 2 | 18 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1867 | 1123 | 2 | 19 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1868 | 1124 | 2 | 20 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1869 | 1125 | 2 | 21 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1870 | 1126 | 2 | 22 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1871 | 1127 | 2 | 23 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1872 | 1128 | 2 | 24 | 47 | 43147 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1873 | 1129 | 2 | 1 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1874 | 1130 | 2 | 2 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1875 | 1131 | 2 | 3 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1876 | 1132 | 2 | 4 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1877 | 1133 | 2 | 5 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1878 | 1134 | 2 | 6 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1879 | 1135 | 2 | 7 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1880 | 1136 | 2 | 8 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1881 | 1137 | 2 | 9 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1882 | 1138 | 2 | 10 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1883 | 1139 | 2 | 11 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1884 | 1140 | 2 | 12 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1885 | 1141 | 2 | 13 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1886 | 1142 | 2 | 14 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1887 | 1143 | 2 | 15 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1888 | 1144 | 2 | 16 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1889 | 1145 | 2 | 17 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1890 | 1146 | 2 | 18 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1891 | 1147 | 2 | 19 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1892 | 1148 | 2 | 20 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1893 | 1149 | 2 | 21 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1894 | 1150 | 2 | 22 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1895 | 1151 | 2 | 23 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1896 | 1152 | 2 | 24 | 48 | 43148 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1897 | 1153 | 2 | 1 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1898 | 1154 | 2 | 2 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1899 | 1155 | 2 | 3 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1900 | 1156 | 2 | 4 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1901 | 1157 | 2 | 5 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1902 | 1158 | 2 | 6 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1903 | 1159 | 2 | 7 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1904 | 1160 | 2 | 8 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1905 | 1161 | 2 | 9 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1906 | 1162 | 2 | 10 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1907 | 1163 | 2 | 11 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1908 | 1164 | 2 | 12 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1909 | 1165 | 2 | 13 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1910 | 1166 | 2 | 14 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1911 | 1167 | 2 | 15 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1912 | 1168 | 2 | 16 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1913 | 1169 | 2 | 17 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1914 | 1170 | 2 | 18 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1915 | 1171 | 2 | 19 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1916 | 1172 | 2 | 20 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1917 | 1173 | 2 | 21 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1918 | 1174 | 2 | 22 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1919 | 1175 | 2 | 23 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1920 | 1176 | 2 | 24 | 49 | 43149 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1921 | 1177 | 2 | 1 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1922 | 1178 | 2 | 2 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1923 | 1179 | 2 | 3 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1924 | 1180 | 2 | 4 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1925 | 1181 | 2 | 5 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1926 | 1182 | 2 | 6 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1927 | 1183 | 2 | 7 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1928 | 1184 | 2 | 8 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1929 | 1185 | 2 | 9 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1930 | 1186 | 2 | 10 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1931 | 1187 | 2 | 11 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1932 | 1188 | 2 | 12 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1933 | 1189 | 2 | 13 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1934 | 1190 | 2 | 14 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1935 | 1191 | 2 | 15 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1936 | 1192 | 2 | 16 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1937 | 1193 | 2 | 17 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1938 | 1194 | 2 | 18 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1939 | 1195 | 2 | 19 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1940 | 1196 | 2 | 20 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1941 | 1197 | 2 | 21 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1942 | 1198 | 2 | 22 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1943 | 1199 | 2 | 23 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1944 | 1200 | 2 | 24 | 50 | 43150 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1945 | 1201 | 2 | 1 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1946 | 1202 | 2 | 2 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1947 | 1203 | 2 | 3 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1948 | 1204 | 2 | 4 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1949 | 1205 | 2 | 5 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1950 | 1206 | 2 | 6 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1951 | 1207 | 2 | 7 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1952 | 1208 | 2 | 8 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1953 | 1209 | 2 | 9 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1954 | 1210 | 2 | 10 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1955 | 1211 | 2 | 11 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1956 | 1212 | 2 | 12 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1957 | 1213 | 2 | 13 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1958 | 1214 | 2 | 14 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1959 | 1215 | 2 | 15 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1960 | 1216 | 2 | 16 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1961 | 1217 | 2 | 17 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1962 | 1218 | 2 | 18 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1963 | 1219 | 2 | 19 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1964 | 1220 | 2 | 20 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1965 | 1221 | 2 | 21 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1966 | 1222 | 2 | 22 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1967 | 1223 | 2 | 23 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1968 | 1224 | 2 | 24 | 51 | 43151 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1969 | 1225 | 2 | 1 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1970 | 1226 | 2 | 2 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1971 | 1227 | 2 | 3 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1972 | 1228 | 2 | 4 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1973 | 1229 | 2 | 5 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1974 | 1230 | 2 | 6 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1975 | 1231 | 2 | 7 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1976 | 1232 | 2 | 8 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1977 | 1233 | 2 | 9 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1978 | 1234 | 2 | 10 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1979 | 1235 | 2 | 11 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1980 | 1236 | 2 | 12 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1981 | 1237 | 2 | 13 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1982 | 1238 | 2 | 14 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1983 | 1239 | 2 | 15 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1984 | 1240 | 2 | 16 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1985 | 1241 | 2 | 17 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1986 | 1242 | 2 | 18 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1987 | 1243 | 2 | 19 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1988 | 1244 | 2 | 20 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1989 | 1245 | 2 | 21 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1990 | 1246 | 2 | 22 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1991 | 1247 | 2 | 23 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1992 | 1248 | 2 | 24 | 52 | 43152 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1993 | 1249 | 2 | 1 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1994 | 1250 | 2 | 2 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1995 | 1251 | 2 | 3 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1996 | 1252 | 2 | 4 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1997 | 1253 | 2 | 5 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1998 | 1254 | 2 | 6 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 1999 | 1255 | 2 | 7 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2000 | 1256 | 2 | 8 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2001 | 1257 | 2 | 9 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2002 | 1258 | 2 | 10 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2003 | 1259 | 2 | 11 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2004 | 1260 | 2 | 12 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2005 | 1261 | 2 | 13 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2006 | 1262 | 2 | 14 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2007 | 1263 | 2 | 15 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2008 | 1264 | 2 | 16 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2009 | 1265 | 2 | 17 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2010 | 1266 | 2 | 18 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2011 | 1267 | 2 | 19 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2012 | 1268 | 2 | 20 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2013 | 1269 | 2 | 21 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2014 | 1270 | 2 | 22 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2015 | 1271 | 2 | 23 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2016 | 1272 | 2 | 24 | 53 | 43153 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2017 | 1273 | 2 | 1 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2018 | 1274 | 2 | 2 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2019 | 1275 | 2 | 3 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2020 | 1276 | 2 | 4 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2021 | 1277 | 2 | 5 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2022 | 1278 | 2 | 6 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2023 | 1279 | 2 | 7 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2024 | 1280 | 2 | 8 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2025 | 1281 | 2 | 9 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2026 | 1282 | 2 | 10 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2027 | 1283 | 2 | 11 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2028 | 1284 | 2 | 12 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2029 | 1285 | 2 | 13 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2030 | 1286 | 2 | 14 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2031 | 1287 | 2 | 15 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2032 | 1288 | 2 | 16 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2033 | 1289 | 2 | 17 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2034 | 1290 | 2 | 18 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2035 | 1291 | 2 | 19 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2036 | 1292 | 2 | 20 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2037 | 1293 | 2 | 21 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2038 | 1294 | 2 | 22 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2039 | 1295 | 2 | 23 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2040 | 1296 | 2 | 24 | 54 | 43154 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2041 | 1297 | 2 | 1 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2042 | 1298 | 2 | 2 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2043 | 1299 | 2 | 3 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2044 | 1300 | 2 | 4 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2045 | 1301 | 2 | 5 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2046 | 1302 | 2 | 6 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2047 | 1303 | 2 | 7 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2048 | 1304 | 2 | 8 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2049 | 1305 | 2 | 9 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2050 | 1306 | 2 | 10 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2051 | 1307 | 2 | 11 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2052 | 1308 | 2 | 12 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2053 | 1309 | 2 | 13 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2054 | 1310 | 2 | 14 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2055 | 1311 | 2 | 15 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2056 | 1312 | 2 | 16 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2057 | 1313 | 2 | 17 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2058 | 1314 | 2 | 18 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2059 | 1315 | 2 | 19 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2060 | 1316 | 2 | 20 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2061 | 1317 | 2 | 21 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2062 | 1318 | 2 | 22 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2063 | 1319 | 2 | 23 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2064 | 1320 | 2 | 24 | 55 | 43155 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2065 | 1321 | 2 | 1 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2066 | 1322 | 2 | 2 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2067 | 1323 | 2 | 3 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2068 | 1324 | 2 | 4 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2069 | 1325 | 2 | 5 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2070 | 1326 | 2 | 6 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2071 | 1327 | 2 | 7 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2072 | 1328 | 2 | 8 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2073 | 1329 | 2 | 9 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2074 | 1330 | 2 | 10 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2075 | 1331 | 2 | 11 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2076 | 1332 | 2 | 12 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2077 | 1333 | 2 | 13 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2078 | 1334 | 2 | 14 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2079 | 1335 | 2 | 15 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2080 | 1336 | 2 | 16 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2081 | 1337 | 2 | 17 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2082 | 1338 | 2 | 18 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2083 | 1339 | 2 | 19 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2084 | 1340 | 2 | 20 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2085 | 1341 | 2 | 21 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2086 | 1342 | 2 | 22 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2087 | 1343 | 2 | 23 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2088 | 1344 | 2 | 24 | 56 | 43156 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2089 | 1345 | 2 | 1 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2090 | 1346 | 2 | 2 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2091 | 1347 | 2 | 3 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2092 | 1348 | 2 | 4 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2093 | 1349 | 2 | 5 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2094 | 1350 | 2 | 6 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2095 | 1351 | 2 | 7 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2096 | 1352 | 2 | 8 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2097 | 1353 | 2 | 9 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2098 | 1354 | 2 | 10 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2099 | 1355 | 2 | 11 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2100 | 1356 | 2 | 12 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2101 | 1357 | 2 | 13 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2102 | 1358 | 2 | 14 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2103 | 1359 | 2 | 15 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2104 | 1360 | 2 | 16 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2105 | 1361 | 2 | 17 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2106 | 1362 | 2 | 18 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2107 | 1363 | 2 | 19 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2108 | 1364 | 2 | 20 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2109 | 1365 | 2 | 21 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2110 | 1366 | 2 | 22 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2111 | 1367 | 2 | 23 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2112 | 1368 | 2 | 24 | 57 | 43157 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2113 | 1369 | 2 | 1 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2114 | 1370 | 2 | 2 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2115 | 1371 | 2 | 3 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2116 | 1372 | 2 | 4 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2117 | 1373 | 2 | 5 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2118 | 1374 | 2 | 6 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2119 | 1375 | 2 | 7 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2120 | 1376 | 2 | 8 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2121 | 1377 | 2 | 9 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2122 | 1378 | 2 | 10 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2123 | 1379 | 2 | 11 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2124 | 1380 | 2 | 12 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2125 | 1381 | 2 | 13 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2126 | 1382 | 2 | 14 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2127 | 1383 | 2 | 15 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2128 | 1384 | 2 | 16 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2129 | 1385 | 2 | 17 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2130 | 1386 | 2 | 18 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2131 | 1387 | 2 | 19 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2132 | 1388 | 2 | 20 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2133 | 1389 | 2 | 21 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2134 | 1390 | 2 | 22 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2135 | 1391 | 2 | 23 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2136 | 1392 | 2 | 24 | 58 | 43158 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2137 | 1393 | 2 | 1 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2138 | 1394 | 2 | 2 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2139 | 1395 | 2 | 3 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2140 | 1396 | 2 | 4 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2141 | 1397 | 2 | 5 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2142 | 1398 | 2 | 6 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2143 | 1399 | 2 | 7 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2144 | 1400 | 2 | 8 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2145 | 1401 | 2 | 9 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2146 | 1402 | 2 | 10 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2147 | 1403 | 2 | 11 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2148 | 1404 | 2 | 12 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2149 | 1405 | 2 | 13 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2150 | 1406 | 2 | 14 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2151 | 1407 | 2 | 15 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2152 | 1408 | 2 | 16 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2153 | 1409 | 2 | 17 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2154 | 1410 | 2 | 18 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2155 | 1411 | 2 | 19 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2156 | 1412 | 2 | 20 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2157 | 1413 | 2 | 21 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2158 | 1414 | 2 | 22 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2159 | 1415 | 2 | 23 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2160 | 1416 | 2 | 24 | 59 | 43159 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2161 | 1417 | 3 | 1 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2162 | 1418 | 3 | 2 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2163 | 1419 | 3 | 3 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2164 | 1420 | 3 | 4 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2165 | 1421 | 3 | 5 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2166 | 1422 | 3 | 6 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2167 | 1423 | 3 | 7 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2168 | 1424 | 3 | 8 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2169 | 1425 | 3 | 9 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2170 | 1426 | 3 | 10 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2171 | 1427 | 3 | 11 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2172 | 1428 | 3 | 12 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2173 | 1429 | 3 | 13 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2174 | 1430 | 3 | 14 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2175 | 1431 | 3 | 15 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2176 | 1432 | 3 | 16 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2177 | 1433 | 3 | 17 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2178 | 1434 | 3 | 18 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2179 | 1435 | 3 | 19 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2180 | 1436 | 3 | 20 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2181 | 1437 | 3 | 21 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2182 | 1438 | 3 | 22 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2183 | 1439 | 3 | 23 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2184 | 1440 | 3 | 24 | 60 | 43160 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2185 | 1441 | 3 | 1 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2186 | 1442 | 3 | 2 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2187 | 1443 | 3 | 3 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2188 | 1444 | 3 | 4 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2189 | 1445 | 3 | 5 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2190 | 1446 | 3 | 6 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2191 | 1447 | 3 | 7 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2192 | 1448 | 3 | 8 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2193 | 1449 | 3 | 9 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2194 | 1450 | 3 | 10 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2195 | 1451 | 3 | 11 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2196 | 1452 | 3 | 12 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2197 | 1453 | 3 | 13 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2198 | 1454 | 3 | 14 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2199 | 1455 | 3 | 15 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2200 | 1456 | 3 | 16 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2201 | 1457 | 3 | 17 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2202 | 1458 | 3 | 18 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2203 | 1459 | 3 | 19 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2204 | 1460 | 3 | 20 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2205 | 1461 | 3 | 21 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2206 | 1462 | 3 | 22 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2207 | 1463 | 3 | 23 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2208 | 1464 | 3 | 24 | 61 | 43161 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2209 | 1465 | 3 | 1 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2210 | 1466 | 3 | 2 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2211 | 1467 | 3 | 3 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2212 | 1468 | 3 | 4 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2213 | 1469 | 3 | 5 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2214 | 1470 | 3 | 6 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2215 | 1471 | 3 | 7 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2216 | 1472 | 3 | 8 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2217 | 1473 | 3 | 9 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2218 | 1474 | 3 | 10 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2219 | 1475 | 3 | 11 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2220 | 1476 | 3 | 12 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2221 | 1477 | 3 | 13 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2222 | 1478 | 3 | 14 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2223 | 1479 | 3 | 15 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2224 | 1480 | 3 | 16 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2225 | 1481 | 3 | 17 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2226 | 1482 | 3 | 18 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2227 | 1483 | 3 | 19 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2228 | 1484 | 3 | 20 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2229 | 1485 | 3 | 21 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2230 | 1486 | 3 | 22 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2231 | 1487 | 3 | 23 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2232 | 1488 | 3 | 24 | 62 | 43162 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2233 | 1489 | 3 | 1 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2234 | 1490 | 3 | 2 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2235 | 1491 | 3 | 3 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2236 | 1492 | 3 | 4 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2237 | 1493 | 3 | 5 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2238 | 1494 | 3 | 6 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2239 | 1495 | 3 | 7 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2240 | 1496 | 3 | 8 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2241 | 1497 | 3 | 9 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2242 | 1498 | 3 | 10 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2243 | 1499 | 3 | 11 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2244 | 1500 | 3 | 12 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2245 | 1501 | 3 | 13 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2246 | 1502 | 3 | 14 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2247 | 1503 | 3 | 15 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2248 | 1504 | 3 | 16 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2249 | 1505 | 3 | 17 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2250 | 1506 | 3 | 18 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2251 | 1507 | 3 | 19 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2252 | 1508 | 3 | 20 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2253 | 1509 | 3 | 21 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2254 | 1510 | 3 | 22 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2255 | 1511 | 3 | 23 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2256 | 1512 | 3 | 24 | 63 | 43163 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2257 | 1513 | 3 | 1 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2258 | 1514 | 3 | 2 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2259 | 1515 | 3 | 3 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2260 | 1516 | 3 | 4 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2261 | 1517 | 3 | 5 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2262 | 1518 | 3 | 6 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2263 | 1519 | 3 | 7 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2264 | 1520 | 3 | 8 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2265 | 1521 | 3 | 9 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2266 | 1522 | 3 | 10 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2267 | 1523 | 3 | 11 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2268 | 1524 | 3 | 12 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2269 | 1525 | 3 | 13 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2270 | 1526 | 3 | 14 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2271 | 1527 | 3 | 15 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2272 | 1528 | 3 | 16 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2273 | 1529 | 3 | 17 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2274 | 1530 | 3 | 18 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2275 | 1531 | 3 | 19 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2276 | 1532 | 3 | 20 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2277 | 1533 | 3 | 21 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2278 | 1534 | 3 | 22 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2279 | 1535 | 3 | 23 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2280 | 1536 | 3 | 24 | 64 | 43164 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2281 | 1537 | 3 | 1 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2282 | 1538 | 3 | 2 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2283 | 1539 | 3 | 3 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2284 | 1540 | 3 | 4 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2285 | 1541 | 3 | 5 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2286 | 1542 | 3 | 6 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2287 | 1543 | 3 | 7 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2288 | 1544 | 3 | 8 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2289 | 1545 | 3 | 9 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2290 | 1546 | 3 | 10 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2291 | 1547 | 3 | 11 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2292 | 1548 | 3 | 12 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2293 | 1549 | 3 | 13 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2294 | 1550 | 3 | 14 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2295 | 1551 | 3 | 15 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2296 | 1552 | 3 | 16 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2297 | 1553 | 3 | 17 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2298 | 1554 | 3 | 18 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2299 | 1555 | 3 | 19 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2300 | 1556 | 3 | 20 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2301 | 1557 | 3 | 21 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2302 | 1558 | 3 | 22 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2303 | 1559 | 3 | 23 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2304 | 1560 | 3 | 24 | 65 | 43165 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2305 | 1561 | 3 | 1 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2306 | 1562 | 3 | 2 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2307 | 1563 | 3 | 3 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2308 | 1564 | 3 | 4 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2309 | 1565 | 3 | 5 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2310 | 1566 | 3 | 6 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2311 | 1567 | 3 | 7 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2312 | 1568 | 3 | 8 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2313 | 1569 | 3 | 9 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2314 | 1570 | 3 | 10 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2315 | 1571 | 3 | 11 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2316 | 1572 | 3 | 12 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2317 | 1573 | 3 | 13 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2318 | 1574 | 3 | 14 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2319 | 1575 | 3 | 15 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2320 | 1576 | 3 | 16 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2321 | 1577 | 3 | 17 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2322 | 1578 | 3 | 18 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2323 | 1579 | 3 | 19 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2324 | 1580 | 3 | 20 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2325 | 1581 | 3 | 21 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2326 | 1582 | 3 | 22 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2327 | 1583 | 3 | 23 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2328 | 1584 | 3 | 24 | 66 | 43166 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2329 | 1585 | 3 | 1 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2330 | 1586 | 3 | 2 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2331 | 1587 | 3 | 3 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2332 | 1588 | 3 | 4 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2333 | 1589 | 3 | 5 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2334 | 1590 | 3 | 6 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2335 | 1591 | 3 | 7 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2336 | 1592 | 3 | 8 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2337 | 1593 | 3 | 9 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2338 | 1594 | 3 | 10 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2339 | 1595 | 3 | 11 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2340 | 1596 | 3 | 12 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2341 | 1597 | 3 | 13 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2342 | 1598 | 3 | 14 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2343 | 1599 | 3 | 15 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2344 | 1600 | 3 | 16 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2345 | 1601 | 3 | 17 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2346 | 1602 | 3 | 18 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2347 | 1603 | 3 | 19 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2348 | 1604 | 3 | 20 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2349 | 1605 | 3 | 21 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2350 | 1606 | 3 | 22 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2351 | 1607 | 3 | 23 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2352 | 1608 | 3 | 24 | 67 | 43167 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2353 | 1609 | 3 | 1 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2354 | 1610 | 3 | 2 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2355 | 1611 | 3 | 3 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2356 | 1612 | 3 | 4 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2357 | 1613 | 3 | 5 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2358 | 1614 | 3 | 6 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2359 | 1615 | 3 | 7 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2360 | 1616 | 3 | 8 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2361 | 1617 | 3 | 9 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2362 | 1618 | 3 | 10 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2363 | 1619 | 3 | 11 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2364 | 1620 | 3 | 12 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2365 | 1621 | 3 | 13 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2366 | 1622 | 3 | 14 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2367 | 1623 | 3 | 15 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2368 | 1624 | 3 | 16 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2369 | 1625 | 3 | 17 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2370 | 1626 | 3 | 18 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2371 | 1627 | 3 | 19 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2372 | 1628 | 3 | 20 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2373 | 1629 | 3 | 21 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2374 | 1630 | 3 | 22 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2375 | 1631 | 3 | 23 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2376 | 1632 | 3 | 24 | 68 | 43168 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2377 | 1633 | 3 | 1 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2378 | 1634 | 3 | 2 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2379 | 1635 | 3 | 3 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2380 | 1636 | 3 | 4 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2381 | 1637 | 3 | 5 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2382 | 1638 | 3 | 6 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2383 | 1639 | 3 | 7 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2384 | 1640 | 3 | 8 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2385 | 1641 | 3 | 9 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2386 | 1642 | 3 | 10 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2387 | 1643 | 3 | 11 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2388 | 1644 | 3 | 12 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2389 | 1645 | 3 | 13 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2390 | 1646 | 3 | 14 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2391 | 1647 | 3 | 15 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2392 | 1648 | 3 | 16 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2393 | 1649 | 3 | 17 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2394 | 1650 | 3 | 18 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2395 | 1651 | 3 | 19 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2396 | 1652 | 3 | 20 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2397 | 1653 | 3 | 21 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2398 | 1654 | 3 | 22 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2399 | 1655 | 3 | 23 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2400 | 1656 | 3 | 24 | 69 | 43169 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2401 | 1657 | 3 | 1 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2402 | 1658 | 3 | 2 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2403 | 1659 | 3 | 3 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2404 | 1660 | 3 | 4 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2405 | 1661 | 3 | 5 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2406 | 1662 | 3 | 6 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2407 | 1663 | 3 | 7 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2408 | 1664 | 3 | 8 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2409 | 1665 | 3 | 9 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2410 | 1666 | 3 | 10 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2411 | 1667 | 3 | 11 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2412 | 1668 | 3 | 12 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2413 | 1669 | 3 | 13 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2414 | 1670 | 3 | 14 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2415 | 1671 | 3 | 15 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2416 | 1672 | 3 | 16 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2417 | 1673 | 3 | 17 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2418 | 1674 | 3 | 18 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2419 | 1675 | 3 | 19 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2420 | 1676 | 3 | 20 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2421 | 1677 | 3 | 21 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2422 | 1678 | 3 | 22 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2423 | 1679 | 3 | 23 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2424 | 1680 | 3 | 24 | 70 | 43170 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2425 | 1681 | 3 | 1 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2426 | 1682 | 3 | 2 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2427 | 1683 | 3 | 3 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2428 | 1684 | 3 | 4 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2429 | 1685 | 3 | 5 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2430 | 1686 | 3 | 6 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2431 | 1687 | 3 | 7 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2432 | 1688 | 3 | 8 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2433 | 1689 | 3 | 9 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2434 | 1690 | 3 | 10 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2435 | 1691 | 3 | 11 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2436 | 1692 | 3 | 12 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2437 | 1693 | 3 | 13 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2438 | 1694 | 3 | 14 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2439 | 1695 | 3 | 15 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2440 | 1696 | 3 | 16 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2441 | 1697 | 3 | 17 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2442 | 1698 | 3 | 18 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2443 | 1699 | 3 | 19 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2444 | 1700 | 3 | 20 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2445 | 1701 | 3 | 21 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2446 | 1702 | 3 | 22 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2447 | 1703 | 3 | 23 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2448 | 1704 | 3 | 24 | 71 | 43171 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2449 | 1705 | 3 | 1 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2450 | 1706 | 3 | 2 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2451 | 1707 | 3 | 3 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2452 | 1708 | 3 | 4 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2453 | 1709 | 3 | 5 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2454 | 1710 | 3 | 6 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2455 | 1711 | 3 | 7 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2456 | 1712 | 3 | 8 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2457 | 1713 | 3 | 9 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2458 | 1714 | 3 | 10 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2459 | 1715 | 3 | 11 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2460 | 1716 | 3 | 12 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2461 | 1717 | 3 | 13 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2462 | 1718 | 3 | 14 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2463 | 1719 | 3 | 15 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2464 | 1720 | 3 | 16 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2465 | 1721 | 3 | 17 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2466 | 1722 | 3 | 18 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2467 | 1723 | 3 | 19 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2468 | 1724 | 3 | 20 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2469 | 1725 | 3 | 21 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2470 | 1726 | 3 | 22 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2471 | 1727 | 3 | 23 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2472 | 1728 | 3 | 24 | 72 | 43172 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2473 | 1729 | 3 | 1 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2474 | 1730 | 3 | 2 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2475 | 1731 | 3 | 3 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2476 | 1732 | 3 | 4 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2477 | 1733 | 3 | 5 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2478 | 1734 | 3 | 6 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2479 | 1735 | 3 | 7 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2480 | 1736 | 3 | 8 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2481 | 1737 | 3 | 9 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2482 | 1738 | 3 | 10 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2483 | 1739 | 3 | 11 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2484 | 1740 | 3 | 12 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2485 | 1741 | 3 | 13 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2486 | 1742 | 3 | 14 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2487 | 1743 | 3 | 15 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2488 | 1744 | 3 | 16 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2489 | 1745 | 3 | 17 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2490 | 1746 | 3 | 18 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2491 | 1747 | 3 | 19 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2492 | 1748 | 3 | 20 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2493 | 1749 | 3 | 21 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2494 | 1750 | 3 | 22 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2495 | 1751 | 3 | 23 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2496 | 1752 | 3 | 24 | 73 | 43173 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2497 | 1753 | 3 | 1 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2498 | 1754 | 3 | 2 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2499 | 1755 | 3 | 3 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2500 | 1756 | 3 | 4 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2501 | 1757 | 3 | 5 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2502 | 1758 | 3 | 6 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2503 | 1759 | 3 | 7 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2504 | 1760 | 3 | 8 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2505 | 1761 | 3 | 9 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2506 | 1762 | 3 | 10 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2507 | 1763 | 3 | 11 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2508 | 1764 | 3 | 12 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2509 | 1765 | 3 | 13 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2510 | 1766 | 3 | 14 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2511 | 1767 | 3 | 15 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2512 | 1768 | 3 | 16 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2513 | 1769 | 3 | 17 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2514 | 1770 | 3 | 18 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2515 | 1771 | 3 | 19 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2516 | 1772 | 3 | 20 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2517 | 1773 | 3 | 21 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2518 | 1774 | 3 | 22 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2519 | 1775 | 3 | 23 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2520 | 1776 | 3 | 24 | 74 | 43174 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2521 | 1777 | 3 | 1 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2522 | 1778 | 3 | 2 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2523 | 1779 | 3 | 3 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2524 | 1780 | 3 | 4 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2525 | 1781 | 3 | 5 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2526 | 1782 | 3 | 6 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2527 | 1783 | 3 | 7 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2528 | 1784 | 3 | 8 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2529 | 1785 | 3 | 9 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2530 | 1786 | 3 | 10 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2531 | 1787 | 3 | 11 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2532 | 1788 | 3 | 12 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2533 | 1789 | 3 | 13 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2534 | 1790 | 3 | 14 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2535 | 1791 | 3 | 15 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2536 | 1792 | 3 | 16 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2537 | 1793 | 3 | 17 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2538 | 1794 | 3 | 18 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2539 | 1795 | 3 | 19 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2540 | 1796 | 3 | 20 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2541 | 1797 | 3 | 21 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2542 | 1798 | 3 | 22 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2543 | 1799 | 3 | 23 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2544 | 1800 | 3 | 24 | 75 | 43175 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2545 | 1801 | 3 | 1 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2546 | 1802 | 3 | 2 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2547 | 1803 | 3 | 3 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2548 | 1804 | 3 | 4 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2549 | 1805 | 3 | 5 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2550 | 1806 | 3 | 6 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2551 | 1807 | 3 | 7 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2552 | 1808 | 3 | 8 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2553 | 1809 | 3 | 9 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2554 | 1810 | 3 | 10 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2555 | 1811 | 3 | 11 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2556 | 1812 | 3 | 12 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2557 | 1813 | 3 | 13 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2558 | 1814 | 3 | 14 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2559 | 1815 | 3 | 15 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2560 | 1816 | 3 | 16 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2561 | 1817 | 3 | 17 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2562 | 1818 | 3 | 18 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2563 | 1819 | 3 | 19 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2564 | 1820 | 3 | 20 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2565 | 1821 | 3 | 21 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2566 | 1822 | 3 | 22 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2567 | 1823 | 3 | 23 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2568 | 1824 | 3 | 24 | 76 | 43176 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2569 | 1825 | 3 | 1 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2570 | 1826 | 3 | 2 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2571 | 1827 | 3 | 3 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2572 | 1828 | 3 | 4 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2573 | 1829 | 3 | 5 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2574 | 1830 | 3 | 6 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2575 | 1831 | 3 | 7 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2576 | 1832 | 3 | 8 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2577 | 1833 | 3 | 9 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2578 | 1834 | 3 | 10 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2579 | 1835 | 3 | 11 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2580 | 1836 | 3 | 12 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2581 | 1837 | 3 | 13 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2582 | 1838 | 3 | 14 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2583 | 1839 | 3 | 15 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2584 | 1840 | 3 | 16 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2585 | 1841 | 3 | 17 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2586 | 1842 | 3 | 18 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2587 | 1843 | 3 | 19 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2588 | 1844 | 3 | 20 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2589 | 1845 | 3 | 21 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2590 | 1846 | 3 | 22 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2591 | 1847 | 3 | 23 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2592 | 1848 | 3 | 24 | 77 | 43177 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2593 | 1849 | 3 | 1 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2594 | 1850 | 3 | 2 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2595 | 1851 | 3 | 3 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2596 | 1852 | 3 | 4 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2597 | 1853 | 3 | 5 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2598 | 1854 | 3 | 6 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2599 | 1855 | 3 | 7 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2600 | 1856 | 3 | 8 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2601 | 1857 | 3 | 9 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2602 | 1858 | 3 | 10 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2603 | 1859 | 3 | 11 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2604 | 1860 | 3 | 12 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2605 | 1861 | 3 | 13 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2606 | 1862 | 3 | 14 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2607 | 1863 | 3 | 15 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2608 | 1864 | 3 | 16 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2609 | 1865 | 3 | 17 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2610 | 1866 | 3 | 18 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2611 | 1867 | 3 | 19 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2612 | 1868 | 3 | 20 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2613 | 1869 | 3 | 21 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2614 | 1870 | 3 | 22 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2615 | 1871 | 3 | 23 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2616 | 1872 | 3 | 24 | 78 | 43178 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2617 | 1873 | 3 | 1 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2618 | 1874 | 3 | 2 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2619 | 1875 | 3 | 3 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2620 | 1876 | 3 | 4 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2621 | 1877 | 3 | 5 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2622 | 1878 | 3 | 6 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2623 | 1879 | 3 | 7 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2624 | 1880 | 3 | 8 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2625 | 1881 | 3 | 9 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2626 | 1882 | 3 | 10 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2627 | 1883 | 3 | 11 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2628 | 1884 | 3 | 12 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2629 | 1885 | 3 | 13 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2630 | 1886 | 3 | 14 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2631 | 1887 | 3 | 15 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2632 | 1888 | 3 | 16 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2633 | 1889 | 3 | 17 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2634 | 1890 | 3 | 18 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2635 | 1891 | 3 | 19 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2636 | 1892 | 3 | 20 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2637 | 1893 | 3 | 21 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2638 | 1894 | 3 | 22 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2639 | 1895 | 3 | 23 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2640 | 1896 | 3 | 24 | 79 | 43179 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2641 | 1897 | 3 | 1 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2642 | 1898 | 3 | 2 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2643 | 1899 | 3 | 3 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2644 | 1900 | 3 | 4 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2645 | 1901 | 3 | 5 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2646 | 1902 | 3 | 6 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2647 | 1903 | 3 | 7 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2648 | 1904 | 3 | 8 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2649 | 1905 | 3 | 9 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2650 | 1906 | 3 | 10 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2651 | 1907 | 3 | 11 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2652 | 1908 | 3 | 12 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2653 | 1909 | 3 | 13 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2654 | 1910 | 3 | 14 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2655 | 1911 | 3 | 15 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2656 | 1912 | 3 | 16 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2657 | 1913 | 3 | 17 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2658 | 1914 | 3 | 18 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2659 | 1915 | 3 | 19 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2660 | 1916 | 3 | 20 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2661 | 1917 | 3 | 21 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2662 | 1918 | 3 | 22 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2663 | 1919 | 3 | 23 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2664 | 1920 | 3 | 24 | 80 | 43180 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2665 | 1921 | 3 | 1 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2666 | 1922 | 3 | 2 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2667 | 1923 | 3 | 3 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2668 | 1924 | 3 | 4 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2669 | 1925 | 3 | 5 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2670 | 1926 | 3 | 6 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2671 | 1927 | 3 | 7 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2672 | 1928 | 3 | 8 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2673 | 1929 | 3 | 9 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2674 | 1930 | 3 | 10 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2675 | 1931 | 3 | 11 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2676 | 1932 | 3 | 12 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2677 | 1933 | 3 | 13 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2678 | 1934 | 3 | 14 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2679 | 1935 | 3 | 15 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2680 | 1936 | 3 | 16 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2681 | 1937 | 3 | 17 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2682 | 1938 | 3 | 18 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2683 | 1939 | 3 | 19 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2684 | 1940 | 3 | 20 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2685 | 1941 | 3 | 21 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2686 | 1942 | 3 | 22 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2687 | 1943 | 3 | 23 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2688 | 1944 | 3 | 24 | 81 | 43181 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2689 | 1945 | 3 | 1 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2690 | 1946 | 3 | 2 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2691 | 1947 | 3 | 3 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2692 | 1948 | 3 | 4 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2693 | 1949 | 3 | 5 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2694 | 1950 | 3 | 6 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2695 | 1951 | 3 | 7 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2696 | 1952 | 3 | 8 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2697 | 1953 | 3 | 9 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2698 | 1954 | 3 | 10 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2699 | 1955 | 3 | 11 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2700 | 1956 | 3 | 12 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2701 | 1957 | 3 | 13 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2702 | 1958 | 3 | 14 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2703 | 1959 | 3 | 15 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2704 | 1960 | 3 | 16 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2705 | 1961 | 3 | 17 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2706 | 1962 | 3 | 18 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2707 | 1963 | 3 | 19 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2708 | 1964 | 3 | 20 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2709 | 1965 | 3 | 21 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2710 | 1966 | 3 | 22 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2711 | 1967 | 3 | 23 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2712 | 1968 | 3 | 24 | 82 | 43182 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2713 | 1969 | 3 | 1 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2714 | 1970 | 3 | 2 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2715 | 1971 | 3 | 3 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2716 | 1972 | 3 | 4 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2717 | 1973 | 3 | 5 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2718 | 1974 | 3 | 6 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2719 | 1975 | 3 | 7 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2720 | 1976 | 3 | 8 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2721 | 1977 | 3 | 9 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2722 | 1978 | 3 | 10 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2723 | 1979 | 3 | 11 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2724 | 1980 | 3 | 12 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2725 | 1981 | 3 | 13 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2726 | 1982 | 3 | 14 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2727 | 1983 | 3 | 15 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2728 | 1984 | 3 | 16 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2729 | 1985 | 3 | 17 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2730 | 1986 | 3 | 18 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2731 | 1987 | 3 | 19 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2732 | 1988 | 3 | 20 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2733 | 1989 | 3 | 21 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2734 | 1990 | 3 | 22 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2735 | 1991 | 3 | 23 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2736 | 1992 | 3 | 24 | 83 | 43183 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2737 | 1993 | 3 | 1 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2738 | 1994 | 3 | 2 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2739 | 1995 | 3 | 3 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2740 | 1996 | 3 | 4 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2741 | 1997 | 3 | 5 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2742 | 1998 | 3 | 6 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2743 | 1999 | 3 | 7 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2744 | 2000 | 3 | 8 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2745 | 2001 | 3 | 9 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2746 | 2002 | 3 | 10 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2747 | 2003 | 3 | 11 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2748 | 2004 | 3 | 12 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2749 | 2005 | 3 | 13 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2750 | 2006 | 3 | 14 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2751 | 2007 | 3 | 15 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2752 | 2008 | 3 | 16 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2753 | 2009 | 3 | 17 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2754 | 2010 | 3 | 18 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2755 | 2011 | 3 | 19 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2756 | 2012 | 3 | 20 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2757 | 2013 | 3 | 21 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2758 | 2014 | 3 | 22 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2759 | 2015 | 3 | 23 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2760 | 2016 | 3 | 24 | 84 | 43184 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2761 | 2017 | 3 | 1 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2762 | 2018 | 3 | 2 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2763 | 2019 | 3 | 3 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2764 | 2020 | 3 | 4 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2765 | 2021 | 3 | 5 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2766 | 2022 | 3 | 6 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2767 | 2023 | 3 | 7 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2768 | 2024 | 3 | 8 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2769 | 2025 | 3 | 9 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2770 | 2026 | 3 | 10 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2771 | 2027 | 3 | 11 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2772 | 2028 | 3 | 12 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2773 | 2029 | 3 | 13 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2774 | 2030 | 3 | 14 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2775 | 2031 | 3 | 15 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2776 | 2032 | 3 | 16 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2777 | 2033 | 3 | 17 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2778 | 2034 | 3 | 18 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2779 | 2035 | 3 | 19 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2780 | 2036 | 3 | 20 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2781 | 2037 | 3 | 21 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2782 | 2038 | 3 | 22 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2783 | 2039 | 3 | 23 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2784 | 2040 | 3 | 24 | 85 | 43185 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2785 | 2041 | 3 | 1 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2786 | 2042 | 3 | 2 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2787 | 2043 | 3 | 3 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2788 | 2044 | 3 | 4 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2789 | 2045 | 3 | 5 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2790 | 2046 | 3 | 6 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2791 | 2047 | 3 | 7 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2792 | 2048 | 3 | 8 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2793 | 2049 | 3 | 9 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2794 | 2050 | 3 | 10 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2795 | 2051 | 3 | 11 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2796 | 2052 | 3 | 12 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2797 | 2053 | 3 | 13 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2798 | 2054 | 3 | 14 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2799 | 2055 | 3 | 15 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2800 | 2056 | 3 | 16 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2801 | 2057 | 3 | 17 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2802 | 2058 | 3 | 18 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2803 | 2059 | 3 | 19 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2804 | 2060 | 3 | 20 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2805 | 2061 | 3 | 21 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2806 | 2062 | 3 | 22 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2807 | 2063 | 3 | 23 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2808 | 2064 | 3 | 24 | 86 | 43186 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2809 | 2065 | 3 | 1 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2810 | 2066 | 3 | 2 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2811 | 2067 | 3 | 3 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2812 | 2068 | 3 | 4 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2813 | 2069 | 3 | 5 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2814 | 2070 | 3 | 6 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2815 | 2071 | 3 | 7 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2816 | 2072 | 3 | 8 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2817 | 2073 | 3 | 9 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2818 | 2074 | 3 | 10 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2819 | 2075 | 3 | 11 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2820 | 2076 | 3 | 12 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2821 | 2077 | 3 | 13 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2822 | 2078 | 3 | 14 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2823 | 2079 | 3 | 15 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2824 | 2080 | 3 | 16 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2825 | 2081 | 3 | 17 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2826 | 2082 | 3 | 18 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2827 | 2083 | 3 | 19 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2828 | 2084 | 3 | 20 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2829 | 2085 | 3 | 21 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2830 | 2086 | 3 | 22 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2831 | 2087 | 3 | 23 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2832 | 2088 | 3 | 24 | 87 | 43187 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2833 | 2089 | 3 | 1 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2834 | 2090 | 3 | 2 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2835 | 2091 | 3 | 3 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2836 | 2092 | 3 | 4 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2837 | 2093 | 3 | 5 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2838 | 2094 | 3 | 6 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2839 | 2095 | 3 | 7 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2840 | 2096 | 3 | 8 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2841 | 2097 | 3 | 9 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2842 | 2098 | 3 | 10 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2843 | 2099 | 3 | 11 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2844 | 2100 | 3 | 12 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2845 | 2101 | 3 | 13 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2846 | 2102 | 3 | 14 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2847 | 2103 | 3 | 15 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2848 | 2104 | 3 | 16 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2849 | 2105 | 3 | 17 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2850 | 2106 | 3 | 18 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2851 | 2107 | 3 | 19 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2852 | 2108 | 3 | 20 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2853 | 2109 | 3 | 21 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2854 | 2110 | 3 | 22 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2855 | 2111 | 3 | 23 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2856 | 2112 | 3 | 24 | 88 | 43188 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2857 | 2113 | 3 | 1 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2858 | 2114 | 3 | 2 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2859 | 2115 | 3 | 3 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2860 | 2116 | 3 | 4 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2861 | 2117 | 3 | 5 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2862 | 2118 | 3 | 6 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2863 | 2119 | 3 | 7 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2864 | 2120 | 3 | 8 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2865 | 2121 | 3 | 9 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2866 | 2122 | 3 | 10 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2867 | 2123 | 3 | 11 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2868 | 2124 | 3 | 12 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2869 | 2125 | 3 | 13 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2870 | 2126 | 3 | 14 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2871 | 2127 | 3 | 15 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2872 | 2128 | 3 | 16 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2873 | 2129 | 3 | 17 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2874 | 2130 | 3 | 18 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2875 | 2131 | 3 | 19 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2876 | 2132 | 3 | 20 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2877 | 2133 | 3 | 21 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2878 | 2134 | 3 | 22 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2879 | 2135 | 3 | 23 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2880 | 2136 | 3 | 24 | 89 | 43189 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2881 | 2137 | 3 | 1 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2882 | 2138 | 3 | 2 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2883 | 2139 | 3 | 3 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2884 | 2140 | 3 | 4 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2885 | 2141 | 3 | 5 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2886 | 2142 | 3 | 6 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2887 | 2143 | 3 | 7 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2888 | 2144 | 3 | 8 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2889 | 2145 | 3 | 9 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2890 | 2146 | 3 | 10 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2891 | 2147 | 3 | 11 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2892 | 2148 | 3 | 12 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2893 | 2149 | 3 | 13 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2894 | 2150 | 3 | 14 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2895 | 2151 | 3 | 15 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2896 | 2152 | 3 | 16 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2897 | 2153 | 3 | 17 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2898 | 2154 | 3 | 18 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2899 | 2155 | 3 | 19 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2900 | 2156 | 3 | 20 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2901 | 2157 | 3 | 21 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2902 | 2158 | 3 | 22 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2903 | 2159 | 3 | 23 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2904 | 2160 | 3 | 24 | 90 | 43190 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2905 | 2161 | 4 | 1 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2906 | 2162 | 4 | 2 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2907 | 2163 | 4 | 3 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2908 | 2164 | 4 | 4 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2909 | 2165 | 4 | 5 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2910 | 2166 | 4 | 6 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2911 | 2167 | 4 | 7 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2912 | 2168 | 4 | 8 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2913 | 2169 | 4 | 9 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2914 | 2170 | 4 | 10 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2915 | 2171 | 4 | 11 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2916 | 2172 | 4 | 12 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2917 | 2173 | 4 | 13 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2918 | 2174 | 4 | 14 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2919 | 2175 | 4 | 15 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2920 | 2176 | 4 | 16 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2921 | 2177 | 4 | 17 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2922 | 2178 | 4 | 18 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2923 | 2179 | 4 | 19 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2924 | 2180 | 4 | 20 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2925 | 2181 | 4 | 21 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2926 | 2182 | 4 | 22 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2927 | 2183 | 4 | 23 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2928 | 2184 | 4 | 24 | 91 | 43191 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2929 | 2185 | 4 | 1 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2930 | 2186 | 4 | 2 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2931 | 2187 | 4 | 3 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2932 | 2188 | 4 | 4 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2933 | 2189 | 4 | 5 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2934 | 2190 | 4 | 6 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2935 | 2191 | 4 | 7 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2936 | 2192 | 4 | 8 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2937 | 2193 | 4 | 9 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2938 | 2194 | 4 | 10 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2939 | 2195 | 4 | 11 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2940 | 2196 | 4 | 12 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2941 | 2197 | 4 | 13 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2942 | 2198 | 4 | 14 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2943 | 2199 | 4 | 15 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2944 | 2200 | 4 | 16 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2945 | 2201 | 4 | 17 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2946 | 2202 | 4 | 18 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2947 | 2203 | 4 | 19 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2948 | 2204 | 4 | 20 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2949 | 2205 | 4 | 21 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2950 | 2206 | 4 | 22 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2951 | 2207 | 4 | 23 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2952 | 2208 | 4 | 24 | 92 | 43192 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2953 | 2209 | 4 | 1 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2954 | 2210 | 4 | 2 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2955 | 2211 | 4 | 3 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2956 | 2212 | 4 | 4 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2957 | 2213 | 4 | 5 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2958 | 2214 | 4 | 6 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2959 | 2215 | 4 | 7 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2960 | 2216 | 4 | 8 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2961 | 2217 | 4 | 9 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2962 | 2218 | 4 | 10 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2963 | 2219 | 4 | 11 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2964 | 2220 | 4 | 12 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2965 | 2221 | 4 | 13 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2966 | 2222 | 4 | 14 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2967 | 2223 | 4 | 15 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2968 | 2224 | 4 | 16 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2969 | 2225 | 4 | 17 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2970 | 2226 | 4 | 18 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2971 | 2227 | 4 | 19 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2972 | 2228 | 4 | 20 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2973 | 2229 | 4 | 21 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2974 | 2230 | 4 | 22 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2975 | 2231 | 4 | 23 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2976 | 2232 | 4 | 24 | 93 | 43193 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2977 | 2233 | 4 | 1 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2978 | 2234 | 4 | 2 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2979 | 2235 | 4 | 3 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2980 | 2236 | 4 | 4 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2981 | 2237 | 4 | 5 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2982 | 2238 | 4 | 6 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2983 | 2239 | 4 | 7 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2984 | 2240 | 4 | 8 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2985 | 2241 | 4 | 9 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2986 | 2242 | 4 | 10 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2987 | 2243 | 4 | 11 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2988 | 2244 | 4 | 12 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2989 | 2245 | 4 | 13 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2990 | 2246 | 4 | 14 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2991 | 2247 | 4 | 15 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2992 | 2248 | 4 | 16 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2993 | 2249 | 4 | 17 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2994 | 2250 | 4 | 18 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2995 | 2251 | 4 | 19 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2996 | 2252 | 4 | 20 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2997 | 2253 | 4 | 21 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2998 | 2254 | 4 | 22 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 2999 | 2255 | 4 | 23 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3000 | 2256 | 4 | 24 | 94 | 43194 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3001 | 2257 | 4 | 1 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3002 | 2258 | 4 | 2 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3003 | 2259 | 4 | 3 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3004 | 2260 | 4 | 4 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3005 | 2261 | 4 | 5 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3006 | 2262 | 4 | 6 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3007 | 2263 | 4 | 7 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3008 | 2264 | 4 | 8 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3009 | 2265 | 4 | 9 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3010 | 2266 | 4 | 10 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3011 | 2267 | 4 | 11 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3012 | 2268 | 4 | 12 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3013 | 2269 | 4 | 13 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3014 | 2270 | 4 | 14 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3015 | 2271 | 4 | 15 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3016 | 2272 | 4 | 16 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3017 | 2273 | 4 | 17 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3018 | 2274 | 4 | 18 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3019 | 2275 | 4 | 19 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3020 | 2276 | 4 | 20 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3021 | 2277 | 4 | 21 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3022 | 2278 | 4 | 22 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3023 | 2279 | 4 | 23 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3024 | 2280 | 4 | 24 | 95 | 43195 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3025 | 2281 | 4 | 1 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3026 | 2282 | 4 | 2 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3027 | 2283 | 4 | 3 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3028 | 2284 | 4 | 4 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3029 | 2285 | 4 | 5 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3030 | 2286 | 4 | 6 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3031 | 2287 | 4 | 7 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3032 | 2288 | 4 | 8 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3033 | 2289 | 4 | 9 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3034 | 2290 | 4 | 10 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3035 | 2291 | 4 | 11 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3036 | 2292 | 4 | 12 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3037 | 2293 | 4 | 13 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3038 | 2294 | 4 | 14 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3039 | 2295 | 4 | 15 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3040 | 2296 | 4 | 16 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3041 | 2297 | 4 | 17 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3042 | 2298 | 4 | 18 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3043 | 2299 | 4 | 19 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3044 | 2300 | 4 | 20 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3045 | 2301 | 4 | 21 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3046 | 2302 | 4 | 22 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3047 | 2303 | 4 | 23 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3048 | 2304 | 4 | 24 | 96 | 43196 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3049 | 2305 | 4 | 1 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3050 | 2306 | 4 | 2 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3051 | 2307 | 4 | 3 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3052 | 2308 | 4 | 4 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3053 | 2309 | 4 | 5 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3054 | 2310 | 4 | 6 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3055 | 2311 | 4 | 7 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3056 | 2312 | 4 | 8 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3057 | 2313 | 4 | 9 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3058 | 2314 | 4 | 10 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3059 | 2315 | 4 | 11 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3060 | 2316 | 4 | 12 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3061 | 2317 | 4 | 13 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3062 | 2318 | 4 | 14 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3063 | 2319 | 4 | 15 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3064 | 2320 | 4 | 16 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3065 | 2321 | 4 | 17 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3066 | 2322 | 4 | 18 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3067 | 2323 | 4 | 19 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3068 | 2324 | 4 | 20 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3069 | 2325 | 4 | 21 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3070 | 2326 | 4 | 22 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3071 | 2327 | 4 | 23 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3072 | 2328 | 4 | 24 | 97 | 43197 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3073 | 2329 | 4 | 1 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3074 | 2330 | 4 | 2 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3075 | 2331 | 4 | 3 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3076 | 2332 | 4 | 4 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3077 | 2333 | 4 | 5 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3078 | 2334 | 4 | 6 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3079 | 2335 | 4 | 7 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3080 | 2336 | 4 | 8 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3081 | 2337 | 4 | 9 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3082 | 2338 | 4 | 10 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3083 | 2339 | 4 | 11 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3084 | 2340 | 4 | 12 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3085 | 2341 | 4 | 13 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3086 | 2342 | 4 | 14 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3087 | 2343 | 4 | 15 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3088 | 2344 | 4 | 16 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3089 | 2345 | 4 | 17 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3090 | 2346 | 4 | 18 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3091 | 2347 | 4 | 19 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3092 | 2348 | 4 | 20 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3093 | 2349 | 4 | 21 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3094 | 2350 | 4 | 22 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3095 | 2351 | 4 | 23 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3096 | 2352 | 4 | 24 | 98 | 43198 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3097 | 2353 | 4 | 1 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3098 | 2354 | 4 | 2 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3099 | 2355 | 4 | 3 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3100 | 2356 | 4 | 4 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3101 | 2357 | 4 | 5 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3102 | 2358 | 4 | 6 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3103 | 2359 | 4 | 7 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3104 | 2360 | 4 | 8 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3105 | 2361 | 4 | 9 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3106 | 2362 | 4 | 10 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3107 | 2363 | 4 | 11 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3108 | 2364 | 4 | 12 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3109 | 2365 | 4 | 13 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3110 | 2366 | 4 | 14 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3111 | 2367 | 4 | 15 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3112 | 2368 | 4 | 16 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3113 | 2369 | 4 | 17 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3114 | 2370 | 4 | 18 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3115 | 2371 | 4 | 19 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3116 | 2372 | 4 | 20 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3117 | 2373 | 4 | 21 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3118 | 2374 | 4 | 22 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3119 | 2375 | 4 | 23 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3120 | 2376 | 4 | 24 | 99 | 43199 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3121 | 2377 | 4 | 1 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3122 | 2378 | 4 | 2 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3123 | 2379 | 4 | 3 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3124 | 2380 | 4 | 4 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3125 | 2381 | 4 | 5 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3126 | 2382 | 4 | 6 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3127 | 2383 | 4 | 7 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3128 | 2384 | 4 | 8 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3129 | 2385 | 4 | 9 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3130 | 2386 | 4 | 10 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3131 | 2387 | 4 | 11 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3132 | 2388 | 4 | 12 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3133 | 2389 | 4 | 13 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3134 | 2390 | 4 | 14 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3135 | 2391 | 4 | 15 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3136 | 2392 | 4 | 16 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3137 | 2393 | 4 | 17 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3138 | 2394 | 4 | 18 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3139 | 2395 | 4 | 19 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3140 | 2396 | 4 | 20 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3141 | 2397 | 4 | 21 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3142 | 2398 | 4 | 22 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3143 | 2399 | 4 | 23 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3144 | 2400 | 4 | 24 | 100 | 43200 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3145 | 2401 | 4 | 1 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3146 | 2402 | 4 | 2 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3147 | 2403 | 4 | 3 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3148 | 2404 | 4 | 4 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3149 | 2405 | 4 | 5 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3150 | 2406 | 4 | 6 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3151 | 2407 | 4 | 7 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3152 | 2408 | 4 | 8 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3153 | 2409 | 4 | 9 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3154 | 2410 | 4 | 10 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3155 | 2411 | 4 | 11 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3156 | 2412 | 4 | 12 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3157 | 2413 | 4 | 13 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3158 | 2414 | 4 | 14 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3159 | 2415 | 4 | 15 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3160 | 2416 | 4 | 16 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3161 | 2417 | 4 | 17 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3162 | 2418 | 4 | 18 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3163 | 2419 | 4 | 19 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3164 | 2420 | 4 | 20 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3165 | 2421 | 4 | 21 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3166 | 2422 | 4 | 22 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3167 | 2423 | 4 | 23 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3168 | 2424 | 4 | 24 | 101 | 43201 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3169 | 2425 | 4 | 1 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3170 | 2426 | 4 | 2 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3171 | 2427 | 4 | 3 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3172 | 2428 | 4 | 4 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3173 | 2429 | 4 | 5 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3174 | 2430 | 4 | 6 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3175 | 2431 | 4 | 7 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3176 | 2432 | 4 | 8 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3177 | 2433 | 4 | 9 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3178 | 2434 | 4 | 10 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3179 | 2435 | 4 | 11 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3180 | 2436 | 4 | 12 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3181 | 2437 | 4 | 13 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3182 | 2438 | 4 | 14 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3183 | 2439 | 4 | 15 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3184 | 2440 | 4 | 16 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3185 | 2441 | 4 | 17 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3186 | 2442 | 4 | 18 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3187 | 2443 | 4 | 19 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3188 | 2444 | 4 | 20 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3189 | 2445 | 4 | 21 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3190 | 2446 | 4 | 22 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3191 | 2447 | 4 | 23 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3192 | 2448 | 4 | 24 | 102 | 43202 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3193 | 2449 | 4 | 1 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3194 | 2450 | 4 | 2 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3195 | 2451 | 4 | 3 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3196 | 2452 | 4 | 4 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3197 | 2453 | 4 | 5 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3198 | 2454 | 4 | 6 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3199 | 2455 | 4 | 7 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3200 | 2456 | 4 | 8 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3201 | 2457 | 4 | 9 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3202 | 2458 | 4 | 10 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3203 | 2459 | 4 | 11 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3204 | 2460 | 4 | 12 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3205 | 2461 | 4 | 13 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3206 | 2462 | 4 | 14 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3207 | 2463 | 4 | 15 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3208 | 2464 | 4 | 16 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3209 | 2465 | 4 | 17 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3210 | 2466 | 4 | 18 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3211 | 2467 | 4 | 19 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3212 | 2468 | 4 | 20 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3213 | 2469 | 4 | 21 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3214 | 2470 | 4 | 22 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3215 | 2471 | 4 | 23 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3216 | 2472 | 4 | 24 | 103 | 43203 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3217 | 2473 | 4 | 1 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3218 | 2474 | 4 | 2 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3219 | 2475 | 4 | 3 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3220 | 2476 | 4 | 4 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3221 | 2477 | 4 | 5 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3222 | 2478 | 4 | 6 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3223 | 2479 | 4 | 7 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3224 | 2480 | 4 | 8 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3225 | 2481 | 4 | 9 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3226 | 2482 | 4 | 10 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3227 | 2483 | 4 | 11 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3228 | 2484 | 4 | 12 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3229 | 2485 | 4 | 13 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3230 | 2486 | 4 | 14 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3231 | 2487 | 4 | 15 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3232 | 2488 | 4 | 16 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3233 | 2489 | 4 | 17 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3234 | 2490 | 4 | 18 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3235 | 2491 | 4 | 19 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3236 | 2492 | 4 | 20 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3237 | 2493 | 4 | 21 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3238 | 2494 | 4 | 22 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3239 | 2495 | 4 | 23 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3240 | 2496 | 4 | 24 | 104 | 43204 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3241 | 2497 | 4 | 1 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3242 | 2498 | 4 | 2 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3243 | 2499 | 4 | 3 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3244 | 2500 | 4 | 4 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3245 | 2501 | 4 | 5 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3246 | 2502 | 4 | 6 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3247 | 2503 | 4 | 7 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3248 | 2504 | 4 | 8 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3249 | 2505 | 4 | 9 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3250 | 2506 | 4 | 10 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3251 | 2507 | 4 | 11 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3252 | 2508 | 4 | 12 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3253 | 2509 | 4 | 13 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3254 | 2510 | 4 | 14 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3255 | 2511 | 4 | 15 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3256 | 2512 | 4 | 16 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3257 | 2513 | 4 | 17 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3258 | 2514 | 4 | 18 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3259 | 2515 | 4 | 19 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3260 | 2516 | 4 | 20 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3261 | 2517 | 4 | 21 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3262 | 2518 | 4 | 22 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3263 | 2519 | 4 | 23 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3264 | 2520 | 4 | 24 | 105 | 43205 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3265 | 2521 | 4 | 1 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3266 | 2522 | 4 | 2 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3267 | 2523 | 4 | 3 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3268 | 2524 | 4 | 4 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3269 | 2525 | 4 | 5 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3270 | 2526 | 4 | 6 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3271 | 2527 | 4 | 7 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3272 | 2528 | 4 | 8 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3273 | 2529 | 4 | 9 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3274 | 2530 | 4 | 10 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3275 | 2531 | 4 | 11 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3276 | 2532 | 4 | 12 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3277 | 2533 | 4 | 13 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3278 | 2534 | 4 | 14 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3279 | 2535 | 4 | 15 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3280 | 2536 | 4 | 16 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3281 | 2537 | 4 | 17 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3282 | 2538 | 4 | 18 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3283 | 2539 | 4 | 19 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3284 | 2540 | 4 | 20 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3285 | 2541 | 4 | 21 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3286 | 2542 | 4 | 22 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3287 | 2543 | 4 | 23 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3288 | 2544 | 4 | 24 | 106 | 43206 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3289 | 2545 | 4 | 1 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3290 | 2546 | 4 | 2 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3291 | 2547 | 4 | 3 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3292 | 2548 | 4 | 4 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3293 | 2549 | 4 | 5 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3294 | 2550 | 4 | 6 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3295 | 2551 | 4 | 7 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3296 | 2552 | 4 | 8 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3297 | 2553 | 4 | 9 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3298 | 2554 | 4 | 10 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3299 | 2555 | 4 | 11 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3300 | 2556 | 4 | 12 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3301 | 2557 | 4 | 13 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3302 | 2558 | 4 | 14 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3303 | 2559 | 4 | 15 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3304 | 2560 | 4 | 16 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3305 | 2561 | 4 | 17 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3306 | 2562 | 4 | 18 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3307 | 2563 | 4 | 19 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3308 | 2564 | 4 | 20 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3309 | 2565 | 4 | 21 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3310 | 2566 | 4 | 22 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3311 | 2567 | 4 | 23 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3312 | 2568 | 4 | 24 | 107 | 43207 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3313 | 2569 | 4 | 1 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3314 | 2570 | 4 | 2 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3315 | 2571 | 4 | 3 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3316 | 2572 | 4 | 4 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3317 | 2573 | 4 | 5 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3318 | 2574 | 4 | 6 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3319 | 2575 | 4 | 7 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3320 | 2576 | 4 | 8 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3321 | 2577 | 4 | 9 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3322 | 2578 | 4 | 10 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3323 | 2579 | 4 | 11 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3324 | 2580 | 4 | 12 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3325 | 2581 | 4 | 13 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3326 | 2582 | 4 | 14 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3327 | 2583 | 4 | 15 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3328 | 2584 | 4 | 16 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3329 | 2585 | 4 | 17 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3330 | 2586 | 4 | 18 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3331 | 2587 | 4 | 19 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3332 | 2588 | 4 | 20 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3333 | 2589 | 4 | 21 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3334 | 2590 | 4 | 22 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3335 | 2591 | 4 | 23 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3336 | 2592 | 4 | 24 | 108 | 43208 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3337 | 2593 | 4 | 1 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3338 | 2594 | 4 | 2 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3339 | 2595 | 4 | 3 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3340 | 2596 | 4 | 4 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3341 | 2597 | 4 | 5 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3342 | 2598 | 4 | 6 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3343 | 2599 | 4 | 7 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3344 | 2600 | 4 | 8 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3345 | 2601 | 4 | 9 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3346 | 2602 | 4 | 10 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3347 | 2603 | 4 | 11 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3348 | 2604 | 4 | 12 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3349 | 2605 | 4 | 13 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3350 | 2606 | 4 | 14 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3351 | 2607 | 4 | 15 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3352 | 2608 | 4 | 16 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3353 | 2609 | 4 | 17 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3354 | 2610 | 4 | 18 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3355 | 2611 | 4 | 19 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3356 | 2612 | 4 | 20 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3357 | 2613 | 4 | 21 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3358 | 2614 | 4 | 22 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3359 | 2615 | 4 | 23 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3360 | 2616 | 4 | 24 | 109 | 43209 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3361 | 2617 | 4 | 1 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3362 | 2618 | 4 | 2 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3363 | 2619 | 4 | 3 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3364 | 2620 | 4 | 4 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3365 | 2621 | 4 | 5 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3366 | 2622 | 4 | 6 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3367 | 2623 | 4 | 7 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3368 | 2624 | 4 | 8 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3369 | 2625 | 4 | 9 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3370 | 2626 | 4 | 10 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3371 | 2627 | 4 | 11 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3372 | 2628 | 4 | 12 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3373 | 2629 | 4 | 13 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3374 | 2630 | 4 | 14 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3375 | 2631 | 4 | 15 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3376 | 2632 | 4 | 16 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3377 | 2633 | 4 | 17 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3378 | 2634 | 4 | 18 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3379 | 2635 | 4 | 19 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3380 | 2636 | 4 | 20 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3381 | 2637 | 4 | 21 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3382 | 2638 | 4 | 22 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3383 | 2639 | 4 | 23 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3384 | 2640 | 4 | 24 | 110 | 43210 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3385 | 2641 | 4 | 1 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3386 | 2642 | 4 | 2 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3387 | 2643 | 4 | 3 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3388 | 2644 | 4 | 4 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3389 | 2645 | 4 | 5 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3390 | 2646 | 4 | 6 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3391 | 2647 | 4 | 7 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3392 | 2648 | 4 | 8 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3393 | 2649 | 4 | 9 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3394 | 2650 | 4 | 10 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3395 | 2651 | 4 | 11 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3396 | 2652 | 4 | 12 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3397 | 2653 | 4 | 13 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3398 | 2654 | 4 | 14 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3399 | 2655 | 4 | 15 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3400 | 2656 | 4 | 16 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3401 | 2657 | 4 | 17 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3402 | 2658 | 4 | 18 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3403 | 2659 | 4 | 19 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3404 | 2660 | 4 | 20 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3405 | 2661 | 4 | 21 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3406 | 2662 | 4 | 22 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3407 | 2663 | 4 | 23 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3408 | 2664 | 4 | 24 | 111 | 43211 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3409 | 2665 | 4 | 1 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3410 | 2666 | 4 | 2 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3411 | 2667 | 4 | 3 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3412 | 2668 | 4 | 4 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3413 | 2669 | 4 | 5 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3414 | 2670 | 4 | 6 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3415 | 2671 | 4 | 7 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3416 | 2672 | 4 | 8 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3417 | 2673 | 4 | 9 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3418 | 2674 | 4 | 10 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3419 | 2675 | 4 | 11 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3420 | 2676 | 4 | 12 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3421 | 2677 | 4 | 13 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3422 | 2678 | 4 | 14 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3423 | 2679 | 4 | 15 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3424 | 2680 | 4 | 16 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3425 | 2681 | 4 | 17 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3426 | 2682 | 4 | 18 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3427 | 2683 | 4 | 19 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3428 | 2684 | 4 | 20 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3429 | 2685 | 4 | 21 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3430 | 2686 | 4 | 22 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3431 | 2687 | 4 | 23 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3432 | 2688 | 4 | 24 | 112 | 43212 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3433 | 2689 | 4 | 1 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3434 | 2690 | 4 | 2 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3435 | 2691 | 4 | 3 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3436 | 2692 | 4 | 4 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3437 | 2693 | 4 | 5 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3438 | 2694 | 4 | 6 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3439 | 2695 | 4 | 7 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3440 | 2696 | 4 | 8 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3441 | 2697 | 4 | 9 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3442 | 2698 | 4 | 10 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3443 | 2699 | 4 | 11 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3444 | 2700 | 4 | 12 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3445 | 2701 | 4 | 13 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3446 | 2702 | 4 | 14 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3447 | 2703 | 4 | 15 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3448 | 2704 | 4 | 16 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3449 | 2705 | 4 | 17 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3450 | 2706 | 4 | 18 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3451 | 2707 | 4 | 19 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3452 | 2708 | 4 | 20 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3453 | 2709 | 4 | 21 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3454 | 2710 | 4 | 22 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3455 | 2711 | 4 | 23 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3456 | 2712 | 4 | 24 | 113 | 43213 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3457 | 2713 | 4 | 1 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3458 | 2714 | 4 | 2 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3459 | 2715 | 4 | 3 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3460 | 2716 | 4 | 4 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3461 | 2717 | 4 | 5 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3462 | 2718 | 4 | 6 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3463 | 2719 | 4 | 7 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3464 | 2720 | 4 | 8 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3465 | 2721 | 4 | 9 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3466 | 2722 | 4 | 10 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3467 | 2723 | 4 | 11 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3468 | 2724 | 4 | 12 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3469 | 2725 | 4 | 13 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3470 | 2726 | 4 | 14 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3471 | 2727 | 4 | 15 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3472 | 2728 | 4 | 16 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3473 | 2729 | 4 | 17 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3474 | 2730 | 4 | 18 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3475 | 2731 | 4 | 19 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3476 | 2732 | 4 | 20 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3477 | 2733 | 4 | 21 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3478 | 2734 | 4 | 22 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3479 | 2735 | 4 | 23 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3480 | 2736 | 4 | 24 | 114 | 43214 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3481 | 2737 | 4 | 1 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3482 | 2738 | 4 | 2 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3483 | 2739 | 4 | 3 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3484 | 2740 | 4 | 4 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3485 | 2741 | 4 | 5 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3486 | 2742 | 4 | 6 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3487 | 2743 | 4 | 7 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3488 | 2744 | 4 | 8 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3489 | 2745 | 4 | 9 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3490 | 2746 | 4 | 10 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3491 | 2747 | 4 | 11 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3492 | 2748 | 4 | 12 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3493 | 2749 | 4 | 13 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3494 | 2750 | 4 | 14 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3495 | 2751 | 4 | 15 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3496 | 2752 | 4 | 16 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3497 | 2753 | 4 | 17 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3498 | 2754 | 4 | 18 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3499 | 2755 | 4 | 19 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3500 | 2756 | 4 | 20 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3501 | 2757 | 4 | 21 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3502 | 2758 | 4 | 22 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3503 | 2759 | 4 | 23 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3504 | 2760 | 4 | 24 | 115 | 43215 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3505 | 2761 | 4 | 1 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3506 | 2762 | 4 | 2 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3507 | 2763 | 4 | 3 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3508 | 2764 | 4 | 4 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3509 | 2765 | 4 | 5 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3510 | 2766 | 4 | 6 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3511 | 2767 | 4 | 7 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3512 | 2768 | 4 | 8 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3513 | 2769 | 4 | 9 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3514 | 2770 | 4 | 10 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3515 | 2771 | 4 | 11 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3516 | 2772 | 4 | 12 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3517 | 2773 | 4 | 13 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3518 | 2774 | 4 | 14 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3519 | 2775 | 4 | 15 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3520 | 2776 | 4 | 16 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3521 | 2777 | 4 | 17 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3522 | 2778 | 4 | 18 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3523 | 2779 | 4 | 19 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3524 | 2780 | 4 | 20 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3525 | 2781 | 4 | 21 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3526 | 2782 | 4 | 22 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3527 | 2783 | 4 | 23 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3528 | 2784 | 4 | 24 | 116 | 43216 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3529 | 2785 | 4 | 1 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3530 | 2786 | 4 | 2 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3531 | 2787 | 4 | 3 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3532 | 2788 | 4 | 4 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3533 | 2789 | 4 | 5 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3534 | 2790 | 4 | 6 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3535 | 2791 | 4 | 7 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3536 | 2792 | 4 | 8 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3537 | 2793 | 4 | 9 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3538 | 2794 | 4 | 10 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3539 | 2795 | 4 | 11 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3540 | 2796 | 4 | 12 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3541 | 2797 | 4 | 13 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3542 | 2798 | 4 | 14 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3543 | 2799 | 4 | 15 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3544 | 2800 | 4 | 16 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3545 | 2801 | 4 | 17 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3546 | 2802 | 4 | 18 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3547 | 2803 | 4 | 19 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3548 | 2804 | 4 | 20 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3549 | 2805 | 4 | 21 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3550 | 2806 | 4 | 22 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3551 | 2807 | 4 | 23 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3552 | 2808 | 4 | 24 | 117 | 43217 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3553 | 2809 | 4 | 1 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3554 | 2810 | 4 | 2 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3555 | 2811 | 4 | 3 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3556 | 2812 | 4 | 4 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3557 | 2813 | 4 | 5 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3558 | 2814 | 4 | 6 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3559 | 2815 | 4 | 7 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3560 | 2816 | 4 | 8 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3561 | 2817 | 4 | 9 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3562 | 2818 | 4 | 10 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3563 | 2819 | 4 | 11 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3564 | 2820 | 4 | 12 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3565 | 2821 | 4 | 13 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3566 | 2822 | 4 | 14 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3567 | 2823 | 4 | 15 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3568 | 2824 | 4 | 16 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3569 | 2825 | 4 | 17 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3570 | 2826 | 4 | 18 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3571 | 2827 | 4 | 19 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3572 | 2828 | 4 | 20 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3573 | 2829 | 4 | 21 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3574 | 2830 | 4 | 22 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3575 | 2831 | 4 | 23 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3576 | 2832 | 4 | 24 | 118 | 43218 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3577 | 2833 | 4 | 1 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3578 | 2834 | 4 | 2 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3579 | 2835 | 4 | 3 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3580 | 2836 | 4 | 4 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3581 | 2837 | 4 | 5 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3582 | 2838 | 4 | 6 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3583 | 2839 | 4 | 7 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3584 | 2840 | 4 | 8 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3585 | 2841 | 4 | 9 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3586 | 2842 | 4 | 10 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3587 | 2843 | 4 | 11 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3588 | 2844 | 4 | 12 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3589 | 2845 | 4 | 13 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3590 | 2846 | 4 | 14 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3591 | 2847 | 4 | 15 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3592 | 2848 | 4 | 16 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3593 | 2849 | 4 | 17 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3594 | 2850 | 4 | 18 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3595 | 2851 | 4 | 19 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3596 | 2852 | 4 | 20 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3597 | 2853 | 4 | 21 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3598 | 2854 | 4 | 22 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3599 | 2855 | 4 | 23 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3600 | 2856 | 4 | 24 | 119 | 43219 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3601 | 2857 | 4 | 1 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3602 | 2858 | 4 | 2 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3603 | 2859 | 4 | 3 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3604 | 2860 | 4 | 4 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3605 | 2861 | 4 | 5 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3606 | 2862 | 4 | 6 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3607 | 2863 | 4 | 7 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3608 | 2864 | 4 | 8 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3609 | 2865 | 4 | 9 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3610 | 2866 | 4 | 10 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3611 | 2867 | 4 | 11 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3612 | 2868 | 4 | 12 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3613 | 2869 | 4 | 13 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3614 | 2870 | 4 | 14 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3615 | 2871 | 4 | 15 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3616 | 2872 | 4 | 16 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3617 | 2873 | 4 | 17 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3618 | 2874 | 4 | 18 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3619 | 2875 | 4 | 19 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3620 | 2876 | 4 | 20 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3621 | 2877 | 4 | 21 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3622 | 2878 | 4 | 22 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3623 | 2879 | 4 | 23 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3624 | 2880 | 4 | 24 | 120 | 43220 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3625 | 2881 | 5 | 1 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3626 | 2882 | 5 | 2 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3627 | 2883 | 5 | 3 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3628 | 2884 | 5 | 4 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3629 | 2885 | 5 | 5 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3630 | 2886 | 5 | 6 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3631 | 2887 | 5 | 7 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3632 | 2888 | 5 | 8 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3633 | 2889 | 5 | 9 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3634 | 2890 | 5 | 10 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3635 | 2891 | 5 | 11 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3636 | 2892 | 5 | 12 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3637 | 2893 | 5 | 13 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3638 | 2894 | 5 | 14 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3639 | 2895 | 5 | 15 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3640 | 2896 | 5 | 16 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3641 | 2897 | 5 | 17 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3642 | 2898 | 5 | 18 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3643 | 2899 | 5 | 19 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3644 | 2900 | 5 | 20 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3645 | 2901 | 5 | 21 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3646 | 2902 | 5 | 22 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3647 | 2903 | 5 | 23 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3648 | 2904 | 5 | 24 | 121 | 43221 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3649 | 2905 | 5 | 1 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3650 | 2906 | 5 | 2 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3651 | 2907 | 5 | 3 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3652 | 2908 | 5 | 4 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3653 | 2909 | 5 | 5 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3654 | 2910 | 5 | 6 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3655 | 2911 | 5 | 7 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3656 | 2912 | 5 | 8 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3657 | 2913 | 5 | 9 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3658 | 2914 | 5 | 10 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3659 | 2915 | 5 | 11 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3660 | 2916 | 5 | 12 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3661 | 2917 | 5 | 13 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3662 | 2918 | 5 | 14 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3663 | 2919 | 5 | 15 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3664 | 2920 | 5 | 16 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3665 | 2921 | 5 | 17 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3666 | 2922 | 5 | 18 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3667 | 2923 | 5 | 19 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3668 | 2924 | 5 | 20 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3669 | 2925 | 5 | 21 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3670 | 2926 | 5 | 22 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3671 | 2927 | 5 | 23 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3672 | 2928 | 5 | 24 | 122 | 43222 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3673 | 2929 | 5 | 1 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3674 | 2930 | 5 | 2 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3675 | 2931 | 5 | 3 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3676 | 2932 | 5 | 4 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3677 | 2933 | 5 | 5 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3678 | 2934 | 5 | 6 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3679 | 2935 | 5 | 7 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3680 | 2936 | 5 | 8 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3681 | 2937 | 5 | 9 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3682 | 2938 | 5 | 10 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3683 | 2939 | 5 | 11 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3684 | 2940 | 5 | 12 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3685 | 2941 | 5 | 13 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3686 | 2942 | 5 | 14 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3687 | 2943 | 5 | 15 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3688 | 2944 | 5 | 16 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3689 | 2945 | 5 | 17 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3690 | 2946 | 5 | 18 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3691 | 2947 | 5 | 19 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3692 | 2948 | 5 | 20 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3693 | 2949 | 5 | 21 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3694 | 2950 | 5 | 22 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3695 | 2951 | 5 | 23 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3696 | 2952 | 5 | 24 | 123 | 43223 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3697 | 2953 | 5 | 1 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3698 | 2954 | 5 | 2 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3699 | 2955 | 5 | 3 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3700 | 2956 | 5 | 4 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3701 | 2957 | 5 | 5 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3702 | 2958 | 5 | 6 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3703 | 2959 | 5 | 7 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3704 | 2960 | 5 | 8 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3705 | 2961 | 5 | 9 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3706 | 2962 | 5 | 10 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3707 | 2963 | 5 | 11 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3708 | 2964 | 5 | 12 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3709 | 2965 | 5 | 13 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3710 | 2966 | 5 | 14 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3711 | 2967 | 5 | 15 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3712 | 2968 | 5 | 16 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3713 | 2969 | 5 | 17 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3714 | 2970 | 5 | 18 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3715 | 2971 | 5 | 19 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3716 | 2972 | 5 | 20 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3717 | 2973 | 5 | 21 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3718 | 2974 | 5 | 22 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3719 | 2975 | 5 | 23 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3720 | 2976 | 5 | 24 | 124 | 43224 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3721 | 2977 | 5 | 1 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3722 | 2978 | 5 | 2 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3723 | 2979 | 5 | 3 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3724 | 2980 | 5 | 4 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3725 | 2981 | 5 | 5 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3726 | 2982 | 5 | 6 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3727 | 2983 | 5 | 7 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3728 | 2984 | 5 | 8 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3729 | 2985 | 5 | 9 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3730 | 2986 | 5 | 10 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3731 | 2987 | 5 | 11 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3732 | 2988 | 5 | 12 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3733 | 2989 | 5 | 13 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3734 | 2990 | 5 | 14 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3735 | 2991 | 5 | 15 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3736 | 2992 | 5 | 16 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3737 | 2993 | 5 | 17 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3738 | 2994 | 5 | 18 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3739 | 2995 | 5 | 19 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3740 | 2996 | 5 | 20 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3741 | 2997 | 5 | 21 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3742 | 2998 | 5 | 22 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3743 | 2999 | 5 | 23 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3744 | 3000 | 5 | 24 | 125 | 43225 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3745 | 3001 | 5 | 1 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3746 | 3002 | 5 | 2 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3747 | 3003 | 5 | 3 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3748 | 3004 | 5 | 4 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3749 | 3005 | 5 | 5 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3750 | 3006 | 5 | 6 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3751 | 3007 | 5 | 7 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3752 | 3008 | 5 | 8 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3753 | 3009 | 5 | 9 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3754 | 3010 | 5 | 10 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3755 | 3011 | 5 | 11 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3756 | 3012 | 5 | 12 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3757 | 3013 | 5 | 13 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3758 | 3014 | 5 | 14 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3759 | 3015 | 5 | 15 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3760 | 3016 | 5 | 16 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3761 | 3017 | 5 | 17 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3762 | 3018 | 5 | 18 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3763 | 3019 | 5 | 19 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3764 | 3020 | 5 | 20 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3765 | 3021 | 5 | 21 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3766 | 3022 | 5 | 22 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3767 | 3023 | 5 | 23 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3768 | 3024 | 5 | 24 | 126 | 43226 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3769 | 3025 | 5 | 1 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3770 | 3026 | 5 | 2 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3771 | 3027 | 5 | 3 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3772 | 3028 | 5 | 4 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3773 | 3029 | 5 | 5 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3774 | 3030 | 5 | 6 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3775 | 3031 | 5 | 7 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3776 | 3032 | 5 | 8 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3777 | 3033 | 5 | 9 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3778 | 3034 | 5 | 10 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3779 | 3035 | 5 | 11 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3780 | 3036 | 5 | 12 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3781 | 3037 | 5 | 13 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3782 | 3038 | 5 | 14 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3783 | 3039 | 5 | 15 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3784 | 3040 | 5 | 16 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3785 | 3041 | 5 | 17 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3786 | 3042 | 5 | 18 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3787 | 3043 | 5 | 19 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3788 | 3044 | 5 | 20 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3789 | 3045 | 5 | 21 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3790 | 3046 | 5 | 22 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3791 | 3047 | 5 | 23 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3792 | 3048 | 5 | 24 | 127 | 43227 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3793 | 3049 | 5 | 1 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3794 | 3050 | 5 | 2 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3795 | 3051 | 5 | 3 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3796 | 3052 | 5 | 4 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3797 | 3053 | 5 | 5 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3798 | 3054 | 5 | 6 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3799 | 3055 | 5 | 7 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3800 | 3056 | 5 | 8 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3801 | 3057 | 5 | 9 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3802 | 3058 | 5 | 10 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3803 | 3059 | 5 | 11 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3804 | 3060 | 5 | 12 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3805 | 3061 | 5 | 13 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3806 | 3062 | 5 | 14 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3807 | 3063 | 5 | 15 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3808 | 3064 | 5 | 16 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3809 | 3065 | 5 | 17 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3810 | 3066 | 5 | 18 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3811 | 3067 | 5 | 19 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3812 | 3068 | 5 | 20 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3813 | 3069 | 5 | 21 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3814 | 3070 | 5 | 22 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3815 | 3071 | 5 | 23 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3816 | 3072 | 5 | 24 | 128 | 43228 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3817 | 3073 | 5 | 1 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3818 | 3074 | 5 | 2 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3819 | 3075 | 5 | 3 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3820 | 3076 | 5 | 4 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3821 | 3077 | 5 | 5 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3822 | 3078 | 5 | 6 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3823 | 3079 | 5 | 7 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3824 | 3080 | 5 | 8 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3825 | 3081 | 5 | 9 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3826 | 3082 | 5 | 10 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3827 | 3083 | 5 | 11 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3828 | 3084 | 5 | 12 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3829 | 3085 | 5 | 13 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3830 | 3086 | 5 | 14 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3831 | 3087 | 5 | 15 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3832 | 3088 | 5 | 16 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3833 | 3089 | 5 | 17 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3834 | 3090 | 5 | 18 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3835 | 3091 | 5 | 19 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3836 | 3092 | 5 | 20 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3837 | 3093 | 5 | 21 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3838 | 3094 | 5 | 22 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3839 | 3095 | 5 | 23 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3840 | 3096 | 5 | 24 | 129 | 43229 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3841 | 3097 | 5 | 1 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3842 | 3098 | 5 | 2 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3843 | 3099 | 5 | 3 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3844 | 3100 | 5 | 4 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3845 | 3101 | 5 | 5 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3846 | 3102 | 5 | 6 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3847 | 3103 | 5 | 7 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3848 | 3104 | 5 | 8 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3849 | 3105 | 5 | 9 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3850 | 3106 | 5 | 10 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3851 | 3107 | 5 | 11 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3852 | 3108 | 5 | 12 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3853 | 3109 | 5 | 13 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3854 | 3110 | 5 | 14 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3855 | 3111 | 5 | 15 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3856 | 3112 | 5 | 16 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3857 | 3113 | 5 | 17 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3858 | 3114 | 5 | 18 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3859 | 3115 | 5 | 19 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3860 | 3116 | 5 | 20 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3861 | 3117 | 5 | 21 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3862 | 3118 | 5 | 22 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3863 | 3119 | 5 | 23 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3864 | 3120 | 5 | 24 | 130 | 43230 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3865 | 3121 | 5 | 1 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3866 | 3122 | 5 | 2 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3867 | 3123 | 5 | 3 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3868 | 3124 | 5 | 4 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3869 | 3125 | 5 | 5 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3870 | 3126 | 5 | 6 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3871 | 3127 | 5 | 7 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3872 | 3128 | 5 | 8 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3873 | 3129 | 5 | 9 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3874 | 3130 | 5 | 10 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3875 | 3131 | 5 | 11 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3876 | 3132 | 5 | 12 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3877 | 3133 | 5 | 13 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3878 | 3134 | 5 | 14 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3879 | 3135 | 5 | 15 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3880 | 3136 | 5 | 16 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3881 | 3137 | 5 | 17 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3882 | 3138 | 5 | 18 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3883 | 3139 | 5 | 19 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3884 | 3140 | 5 | 20 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3885 | 3141 | 5 | 21 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3886 | 3142 | 5 | 22 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3887 | 3143 | 5 | 23 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3888 | 3144 | 5 | 24 | 131 | 43231 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3889 | 3145 | 5 | 1 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3890 | 3146 | 5 | 2 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3891 | 3147 | 5 | 3 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3892 | 3148 | 5 | 4 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3893 | 3149 | 5 | 5 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3894 | 3150 | 5 | 6 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3895 | 3151 | 5 | 7 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3896 | 3152 | 5 | 8 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3897 | 3153 | 5 | 9 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3898 | 3154 | 5 | 10 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3899 | 3155 | 5 | 11 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3900 | 3156 | 5 | 12 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3901 | 3157 | 5 | 13 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3902 | 3158 | 5 | 14 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3903 | 3159 | 5 | 15 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3904 | 3160 | 5 | 16 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3905 | 3161 | 5 | 17 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3906 | 3162 | 5 | 18 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3907 | 3163 | 5 | 19 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3908 | 3164 | 5 | 20 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3909 | 3165 | 5 | 21 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3910 | 3166 | 5 | 22 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3911 | 3167 | 5 | 23 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3912 | 3168 | 5 | 24 | 132 | 43232 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3913 | 3169 | 5 | 1 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3914 | 3170 | 5 | 2 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3915 | 3171 | 5 | 3 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3916 | 3172 | 5 | 4 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3917 | 3173 | 5 | 5 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3918 | 3174 | 5 | 6 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3919 | 3175 | 5 | 7 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3920 | 3176 | 5 | 8 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3921 | 3177 | 5 | 9 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3922 | 3178 | 5 | 10 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3923 | 3179 | 5 | 11 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3924 | 3180 | 5 | 12 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3925 | 3181 | 5 | 13 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3926 | 3182 | 5 | 14 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3927 | 3183 | 5 | 15 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3928 | 3184 | 5 | 16 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3929 | 3185 | 5 | 17 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3930 | 3186 | 5 | 18 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3931 | 3187 | 5 | 19 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3932 | 3188 | 5 | 20 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3933 | 3189 | 5 | 21 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3934 | 3190 | 5 | 22 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3935 | 3191 | 5 | 23 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3936 | 3192 | 5 | 24 | 133 | 43233 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3937 | 3193 | 5 | 1 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3938 | 3194 | 5 | 2 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3939 | 3195 | 5 | 3 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3940 | 3196 | 5 | 4 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3941 | 3197 | 5 | 5 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3942 | 3198 | 5 | 6 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3943 | 3199 | 5 | 7 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3944 | 3200 | 5 | 8 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3945 | 3201 | 5 | 9 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3946 | 3202 | 5 | 10 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3947 | 3203 | 5 | 11 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3948 | 3204 | 5 | 12 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3949 | 3205 | 5 | 13 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3950 | 3206 | 5 | 14 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3951 | 3207 | 5 | 15 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3952 | 3208 | 5 | 16 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3953 | 3209 | 5 | 17 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3954 | 3210 | 5 | 18 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3955 | 3211 | 5 | 19 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3956 | 3212 | 5 | 20 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3957 | 3213 | 5 | 21 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3958 | 3214 | 5 | 22 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3959 | 3215 | 5 | 23 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3960 | 3216 | 5 | 24 | 134 | 43234 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3961 | 3217 | 5 | 1 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3962 | 3218 | 5 | 2 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3963 | 3219 | 5 | 3 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3964 | 3220 | 5 | 4 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3965 | 3221 | 5 | 5 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3966 | 3222 | 5 | 6 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3967 | 3223 | 5 | 7 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3968 | 3224 | 5 | 8 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3969 | 3225 | 5 | 9 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3970 | 3226 | 5 | 10 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3971 | 3227 | 5 | 11 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3972 | 3228 | 5 | 12 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3973 | 3229 | 5 | 13 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3974 | 3230 | 5 | 14 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3975 | 3231 | 5 | 15 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3976 | 3232 | 5 | 16 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3977 | 3233 | 5 | 17 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3978 | 3234 | 5 | 18 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3979 | 3235 | 5 | 19 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3980 | 3236 | 5 | 20 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3981 | 3237 | 5 | 21 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3982 | 3238 | 5 | 22 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3983 | 3239 | 5 | 23 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3984 | 3240 | 5 | 24 | 135 | 43235 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3985 | 3241 | 5 | 1 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3986 | 3242 | 5 | 2 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3987 | 3243 | 5 | 3 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3988 | 3244 | 5 | 4 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3989 | 3245 | 5 | 5 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3990 | 3246 | 5 | 6 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3991 | 3247 | 5 | 7 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3992 | 3248 | 5 | 8 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3993 | 3249 | 5 | 9 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3994 | 3250 | 5 | 10 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3995 | 3251 | 5 | 11 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3996 | 3252 | 5 | 12 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3997 | 3253 | 5 | 13 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3998 | 3254 | 5 | 14 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 3999 | 3255 | 5 | 15 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4000 | 3256 | 5 | 16 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4001 | 3257 | 5 | 17 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4002 | 3258 | 5 | 18 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4003 | 3259 | 5 | 19 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4004 | 3260 | 5 | 20 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4005 | 3261 | 5 | 21 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4006 | 3262 | 5 | 22 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4007 | 3263 | 5 | 23 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4008 | 3264 | 5 | 24 | 136 | 43236 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4009 | 3265 | 5 | 1 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4010 | 3266 | 5 | 2 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4011 | 3267 | 5 | 3 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4012 | 3268 | 5 | 4 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4013 | 3269 | 5 | 5 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4014 | 3270 | 5 | 6 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4015 | 3271 | 5 | 7 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4016 | 3272 | 5 | 8 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4017 | 3273 | 5 | 9 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4018 | 3274 | 5 | 10 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4019 | 3275 | 5 | 11 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4020 | 3276 | 5 | 12 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4021 | 3277 | 5 | 13 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4022 | 3278 | 5 | 14 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4023 | 3279 | 5 | 15 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4024 | 3280 | 5 | 16 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4025 | 3281 | 5 | 17 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4026 | 3282 | 5 | 18 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4027 | 3283 | 5 | 19 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4028 | 3284 | 5 | 20 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4029 | 3285 | 5 | 21 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4030 | 3286 | 5 | 22 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4031 | 3287 | 5 | 23 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4032 | 3288 | 5 | 24 | 137 | 43237 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4033 | 3289 | 5 | 1 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4034 | 3290 | 5 | 2 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4035 | 3291 | 5 | 3 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4036 | 3292 | 5 | 4 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4037 | 3293 | 5 | 5 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4038 | 3294 | 5 | 6 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4039 | 3295 | 5 | 7 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4040 | 3296 | 5 | 8 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4041 | 3297 | 5 | 9 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4042 | 3298 | 5 | 10 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4043 | 3299 | 5 | 11 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4044 | 3300 | 5 | 12 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4045 | 3301 | 5 | 13 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4046 | 3302 | 5 | 14 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4047 | 3303 | 5 | 15 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4048 | 3304 | 5 | 16 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4049 | 3305 | 5 | 17 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4050 | 3306 | 5 | 18 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4051 | 3307 | 5 | 19 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4052 | 3308 | 5 | 20 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4053 | 3309 | 5 | 21 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4054 | 3310 | 5 | 22 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4055 | 3311 | 5 | 23 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4056 | 3312 | 5 | 24 | 138 | 43238 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4057 | 3313 | 5 | 1 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4058 | 3314 | 5 | 2 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4059 | 3315 | 5 | 3 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4060 | 3316 | 5 | 4 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4061 | 3317 | 5 | 5 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4062 | 3318 | 5 | 6 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4063 | 3319 | 5 | 7 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4064 | 3320 | 5 | 8 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4065 | 3321 | 5 | 9 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4066 | 3322 | 5 | 10 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4067 | 3323 | 5 | 11 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4068 | 3324 | 5 | 12 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4069 | 3325 | 5 | 13 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4070 | 3326 | 5 | 14 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4071 | 3327 | 5 | 15 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4072 | 3328 | 5 | 16 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4073 | 3329 | 5 | 17 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4074 | 3330 | 5 | 18 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4075 | 3331 | 5 | 19 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4076 | 3332 | 5 | 20 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4077 | 3333 | 5 | 21 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4078 | 3334 | 5 | 22 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4079 | 3335 | 5 | 23 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4080 | 3336 | 5 | 24 | 139 | 43239 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4081 | 3337 | 5 | 1 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4082 | 3338 | 5 | 2 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4083 | 3339 | 5 | 3 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4084 | 3340 | 5 | 4 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4085 | 3341 | 5 | 5 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4086 | 3342 | 5 | 6 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4087 | 3343 | 5 | 7 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4088 | 3344 | 5 | 8 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4089 | 3345 | 5 | 9 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4090 | 3346 | 5 | 10 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4091 | 3347 | 5 | 11 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4092 | 3348 | 5 | 12 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4093 | 3349 | 5 | 13 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4094 | 3350 | 5 | 14 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4095 | 3351 | 5 | 15 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4096 | 3352 | 5 | 16 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4097 | 3353 | 5 | 17 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4098 | 3354 | 5 | 18 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4099 | 3355 | 5 | 19 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4100 | 3356 | 5 | 20 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4101 | 3357 | 5 | 21 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4102 | 3358 | 5 | 22 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4103 | 3359 | 5 | 23 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4104 | 3360 | 5 | 24 | 140 | 43240 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4105 | 3361 | 5 | 1 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4106 | 3362 | 5 | 2 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4107 | 3363 | 5 | 3 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4108 | 3364 | 5 | 4 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4109 | 3365 | 5 | 5 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4110 | 3366 | 5 | 6 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4111 | 3367 | 5 | 7 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4112 | 3368 | 5 | 8 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4113 | 3369 | 5 | 9 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4114 | 3370 | 5 | 10 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4115 | 3371 | 5 | 11 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4116 | 3372 | 5 | 12 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4117 | 3373 | 5 | 13 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4118 | 3374 | 5 | 14 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4119 | 3375 | 5 | 15 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4120 | 3376 | 5 | 16 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4121 | 3377 | 5 | 17 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4122 | 3378 | 5 | 18 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4123 | 3379 | 5 | 19 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4124 | 3380 | 5 | 20 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4125 | 3381 | 5 | 21 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4126 | 3382 | 5 | 22 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4127 | 3383 | 5 | 23 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4128 | 3384 | 5 | 24 | 141 | 43241 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4129 | 3385 | 5 | 1 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4130 | 3386 | 5 | 2 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4131 | 3387 | 5 | 3 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4132 | 3388 | 5 | 4 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4133 | 3389 | 5 | 5 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4134 | 3390 | 5 | 6 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4135 | 3391 | 5 | 7 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4136 | 3392 | 5 | 8 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4137 | 3393 | 5 | 9 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4138 | 3394 | 5 | 10 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4139 | 3395 | 5 | 11 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4140 | 3396 | 5 | 12 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4141 | 3397 | 5 | 13 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4142 | 3398 | 5 | 14 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4143 | 3399 | 5 | 15 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4144 | 3400 | 5 | 16 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4145 | 3401 | 5 | 17 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4146 | 3402 | 5 | 18 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4147 | 3403 | 5 | 19 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4148 | 3404 | 5 | 20 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4149 | 3405 | 5 | 21 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4150 | 3406 | 5 | 22 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4151 | 3407 | 5 | 23 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4152 | 3408 | 5 | 24 | 142 | 43242 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4153 | 3409 | 5 | 1 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4154 | 3410 | 5 | 2 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4155 | 3411 | 5 | 3 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4156 | 3412 | 5 | 4 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4157 | 3413 | 5 | 5 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4158 | 3414 | 5 | 6 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4159 | 3415 | 5 | 7 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4160 | 3416 | 5 | 8 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4161 | 3417 | 5 | 9 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4162 | 3418 | 5 | 10 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4163 | 3419 | 5 | 11 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4164 | 3420 | 5 | 12 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4165 | 3421 | 5 | 13 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4166 | 3422 | 5 | 14 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4167 | 3423 | 5 | 15 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4168 | 3424 | 5 | 16 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4169 | 3425 | 5 | 17 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4170 | 3426 | 5 | 18 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4171 | 3427 | 5 | 19 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4172 | 3428 | 5 | 20 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4173 | 3429 | 5 | 21 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4174 | 3430 | 5 | 22 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4175 | 3431 | 5 | 23 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4176 | 3432 | 5 | 24 | 143 | 43243 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4177 | 3433 | 5 | 1 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4178 | 3434 | 5 | 2 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4179 | 3435 | 5 | 3 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4180 | 3436 | 5 | 4 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4181 | 3437 | 5 | 5 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4182 | 3438 | 5 | 6 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4183 | 3439 | 5 | 7 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4184 | 3440 | 5 | 8 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4185 | 3441 | 5 | 9 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4186 | 3442 | 5 | 10 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4187 | 3443 | 5 | 11 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4188 | 3444 | 5 | 12 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4189 | 3445 | 5 | 13 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4190 | 3446 | 5 | 14 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4191 | 3447 | 5 | 15 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4192 | 3448 | 5 | 16 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4193 | 3449 | 5 | 17 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4194 | 3450 | 5 | 18 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4195 | 3451 | 5 | 19 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4196 | 3452 | 5 | 20 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4197 | 3453 | 5 | 21 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4198 | 3454 | 5 | 22 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4199 | 3455 | 5 | 23 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4200 | 3456 | 5 | 24 | 144 | 43244 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4201 | 3457 | 5 | 1 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4202 | 3458 | 5 | 2 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4203 | 3459 | 5 | 3 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4204 | 3460 | 5 | 4 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4205 | 3461 | 5 | 5 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4206 | 3462 | 5 | 6 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4207 | 3463 | 5 | 7 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4208 | 3464 | 5 | 8 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4209 | 3465 | 5 | 9 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4210 | 3466 | 5 | 10 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4211 | 3467 | 5 | 11 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4212 | 3468 | 5 | 12 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4213 | 3469 | 5 | 13 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4214 | 3470 | 5 | 14 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4215 | 3471 | 5 | 15 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4216 | 3472 | 5 | 16 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4217 | 3473 | 5 | 17 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4218 | 3474 | 5 | 18 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4219 | 3475 | 5 | 19 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4220 | 3476 | 5 | 20 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4221 | 3477 | 5 | 21 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4222 | 3478 | 5 | 22 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4223 | 3479 | 5 | 23 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4224 | 3480 | 5 | 24 | 145 | 43245 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4225 | 3481 | 5 | 1 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4226 | 3482 | 5 | 2 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4227 | 3483 | 5 | 3 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4228 | 3484 | 5 | 4 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4229 | 3485 | 5 | 5 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4230 | 3486 | 5 | 6 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4231 | 3487 | 5 | 7 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4232 | 3488 | 5 | 8 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4233 | 3489 | 5 | 9 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4234 | 3490 | 5 | 10 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4235 | 3491 | 5 | 11 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4236 | 3492 | 5 | 12 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4237 | 3493 | 5 | 13 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4238 | 3494 | 5 | 14 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4239 | 3495 | 5 | 15 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4240 | 3496 | 5 | 16 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4241 | 3497 | 5 | 17 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4242 | 3498 | 5 | 18 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4243 | 3499 | 5 | 19 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4244 | 3500 | 5 | 20 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4245 | 3501 | 5 | 21 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4246 | 3502 | 5 | 22 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4247 | 3503 | 5 | 23 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4248 | 3504 | 5 | 24 | 146 | 43246 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4249 | 3505 | 5 | 1 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4250 | 3506 | 5 | 2 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4251 | 3507 | 5 | 3 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4252 | 3508 | 5 | 4 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4253 | 3509 | 5 | 5 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4254 | 3510 | 5 | 6 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4255 | 3511 | 5 | 7 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4256 | 3512 | 5 | 8 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4257 | 3513 | 5 | 9 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4258 | 3514 | 5 | 10 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4259 | 3515 | 5 | 11 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4260 | 3516 | 5 | 12 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4261 | 3517 | 5 | 13 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4262 | 3518 | 5 | 14 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4263 | 3519 | 5 | 15 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4264 | 3520 | 5 | 16 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4265 | 3521 | 5 | 17 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4266 | 3522 | 5 | 18 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4267 | 3523 | 5 | 19 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4268 | 3524 | 5 | 20 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4269 | 3525 | 5 | 21 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4270 | 3526 | 5 | 22 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4271 | 3527 | 5 | 23 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4272 | 3528 | 5 | 24 | 147 | 43247 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4273 | 3529 | 5 | 1 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4274 | 3530 | 5 | 2 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4275 | 3531 | 5 | 3 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4276 | 3532 | 5 | 4 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4277 | 3533 | 5 | 5 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4278 | 3534 | 5 | 6 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4279 | 3535 | 5 | 7 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4280 | 3536 | 5 | 8 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4281 | 3537 | 5 | 9 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4282 | 3538 | 5 | 10 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4283 | 3539 | 5 | 11 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4284 | 3540 | 5 | 12 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4285 | 3541 | 5 | 13 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4286 | 3542 | 5 | 14 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4287 | 3543 | 5 | 15 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4288 | 3544 | 5 | 16 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4289 | 3545 | 5 | 17 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4290 | 3546 | 5 | 18 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4291 | 3547 | 5 | 19 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4292 | 3548 | 5 | 20 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4293 | 3549 | 5 | 21 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4294 | 3550 | 5 | 22 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4295 | 3551 | 5 | 23 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4296 | 3552 | 5 | 24 | 148 | 43248 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4297 | 3553 | 5 | 1 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4298 | 3554 | 5 | 2 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4299 | 3555 | 5 | 3 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4300 | 3556 | 5 | 4 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4301 | 3557 | 5 | 5 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4302 | 3558 | 5 | 6 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4303 | 3559 | 5 | 7 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4304 | 3560 | 5 | 8 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4305 | 3561 | 5 | 9 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4306 | 3562 | 5 | 10 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4307 | 3563 | 5 | 11 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4308 | 3564 | 5 | 12 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4309 | 3565 | 5 | 13 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4310 | 3566 | 5 | 14 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4311 | 3567 | 5 | 15 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4312 | 3568 | 5 | 16 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4313 | 3569 | 5 | 17 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4314 | 3570 | 5 | 18 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4315 | 3571 | 5 | 19 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4316 | 3572 | 5 | 20 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4317 | 3573 | 5 | 21 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4318 | 3574 | 5 | 22 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4319 | 3575 | 5 | 23 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4320 | 3576 | 5 | 24 | 149 | 43249 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4321 | 3577 | 5 | 1 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4322 | 3578 | 5 | 2 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4323 | 3579 | 5 | 3 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4324 | 3580 | 5 | 4 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4325 | 3581 | 5 | 5 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4326 | 3582 | 5 | 6 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4327 | 3583 | 5 | 7 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4328 | 3584 | 5 | 8 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4329 | 3585 | 5 | 9 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4330 | 3586 | 5 | 10 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4331 | 3587 | 5 | 11 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4332 | 3588 | 5 | 12 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4333 | 3589 | 5 | 13 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4334 | 3590 | 5 | 14 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4335 | 3591 | 5 | 15 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4336 | 3592 | 5 | 16 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4337 | 3593 | 5 | 17 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4338 | 3594 | 5 | 18 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4339 | 3595 | 5 | 19 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4340 | 3596 | 5 | 20 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4341 | 3597 | 5 | 21 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4342 | 3598 | 5 | 22 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4343 | 3599 | 5 | 23 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4344 | 3600 | 5 | 24 | 150 | 43250 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4345 | 3601 | 5 | 1 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4346 | 3602 | 5 | 2 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4347 | 3603 | 5 | 3 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4348 | 3604 | 5 | 4 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4349 | 3605 | 5 | 5 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4350 | 3606 | 5 | 6 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4351 | 3607 | 5 | 7 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4352 | 3608 | 5 | 8 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4353 | 3609 | 5 | 9 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4354 | 3610 | 5 | 10 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4355 | 3611 | 5 | 11 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4356 | 3612 | 5 | 12 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4357 | 3613 | 5 | 13 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4358 | 3614 | 5 | 14 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4359 | 3615 | 5 | 15 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4360 | 3616 | 5 | 16 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4361 | 3617 | 5 | 17 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4362 | 3618 | 5 | 18 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4363 | 3619 | 5 | 19 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4364 | 3620 | 5 | 20 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4365 | 3621 | 5 | 21 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4366 | 3622 | 5 | 22 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4367 | 3623 | 5 | 23 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4368 | 3624 | 5 | 24 | 151 | 43251 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4369 | 3625 | 6 | 1 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4370 | 3626 | 6 | 2 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4371 | 3627 | 6 | 3 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4372 | 3628 | 6 | 4 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4373 | 3629 | 6 | 5 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4374 | 3630 | 6 | 6 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4375 | 3631 | 6 | 7 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4376 | 3632 | 6 | 8 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4377 | 3633 | 6 | 9 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4378 | 3634 | 6 | 10 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4379 | 3635 | 6 | 11 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4380 | 3636 | 6 | 12 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4381 | 3637 | 6 | 13 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4382 | 3638 | 6 | 14 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4383 | 3639 | 6 | 15 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4384 | 3640 | 6 | 16 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4385 | 3641 | 6 | 17 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4386 | 3642 | 6 | 18 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4387 | 3643 | 6 | 19 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4388 | 3644 | 6 | 20 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4389 | 3645 | 6 | 21 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4390 | 3646 | 6 | 22 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4391 | 3647 | 6 | 23 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4392 | 3648 | 6 | 24 | 152 | 43252 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4393 | 3649 | 6 | 1 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4394 | 3650 | 6 | 2 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4395 | 3651 | 6 | 3 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4396 | 3652 | 6 | 4 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4397 | 3653 | 6 | 5 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4398 | 3654 | 6 | 6 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4399 | 3655 | 6 | 7 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4400 | 3656 | 6 | 8 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4401 | 3657 | 6 | 9 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4402 | 3658 | 6 | 10 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4403 | 3659 | 6 | 11 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4404 | 3660 | 6 | 12 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4405 | 3661 | 6 | 13 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4406 | 3662 | 6 | 14 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4407 | 3663 | 6 | 15 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4408 | 3664 | 6 | 16 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4409 | 3665 | 6 | 17 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4410 | 3666 | 6 | 18 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4411 | 3667 | 6 | 19 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4412 | 3668 | 6 | 20 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4413 | 3669 | 6 | 21 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4414 | 3670 | 6 | 22 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4415 | 3671 | 6 | 23 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4416 | 3672 | 6 | 24 | 153 | 43253 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4417 | 3673 | 6 | 1 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4418 | 3674 | 6 | 2 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4419 | 3675 | 6 | 3 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4420 | 3676 | 6 | 4 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4421 | 3677 | 6 | 5 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4422 | 3678 | 6 | 6 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4423 | 3679 | 6 | 7 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4424 | 3680 | 6 | 8 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4425 | 3681 | 6 | 9 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4426 | 3682 | 6 | 10 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4427 | 3683 | 6 | 11 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4428 | 3684 | 6 | 12 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4429 | 3685 | 6 | 13 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4430 | 3686 | 6 | 14 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4431 | 3687 | 6 | 15 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4432 | 3688 | 6 | 16 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4433 | 3689 | 6 | 17 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4434 | 3690 | 6 | 18 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4435 | 3691 | 6 | 19 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4436 | 3692 | 6 | 20 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4437 | 3693 | 6 | 21 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4438 | 3694 | 6 | 22 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4439 | 3695 | 6 | 23 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4440 | 3696 | 6 | 24 | 154 | 43254 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4441 | 3697 | 6 | 1 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4442 | 3698 | 6 | 2 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4443 | 3699 | 6 | 3 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4444 | 3700 | 6 | 4 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4445 | 3701 | 6 | 5 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4446 | 3702 | 6 | 6 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4447 | 3703 | 6 | 7 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4448 | 3704 | 6 | 8 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4449 | 3705 | 6 | 9 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4450 | 3706 | 6 | 10 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4451 | 3707 | 6 | 11 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4452 | 3708 | 6 | 12 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4453 | 3709 | 6 | 13 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4454 | 3710 | 6 | 14 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4455 | 3711 | 6 | 15 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4456 | 3712 | 6 | 16 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4457 | 3713 | 6 | 17 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4458 | 3714 | 6 | 18 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4459 | 3715 | 6 | 19 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4460 | 3716 | 6 | 20 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4461 | 3717 | 6 | 21 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4462 | 3718 | 6 | 22 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4463 | 3719 | 6 | 23 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4464 | 3720 | 6 | 24 | 155 | 43255 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4465 | 3721 | 6 | 1 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4466 | 3722 | 6 | 2 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4467 | 3723 | 6 | 3 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4468 | 3724 | 6 | 4 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4469 | 3725 | 6 | 5 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4470 | 3726 | 6 | 6 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4471 | 3727 | 6 | 7 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4472 | 3728 | 6 | 8 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4473 | 3729 | 6 | 9 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4474 | 3730 | 6 | 10 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4475 | 3731 | 6 | 11 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4476 | 3732 | 6 | 12 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4477 | 3733 | 6 | 13 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4478 | 3734 | 6 | 14 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4479 | 3735 | 6 | 15 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4480 | 3736 | 6 | 16 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4481 | 3737 | 6 | 17 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4482 | 3738 | 6 | 18 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4483 | 3739 | 6 | 19 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4484 | 3740 | 6 | 20 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4485 | 3741 | 6 | 21 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4486 | 3742 | 6 | 22 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4487 | 3743 | 6 | 23 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4488 | 3744 | 6 | 24 | 156 | 43256 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4489 | 3745 | 6 | 1 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4490 | 3746 | 6 | 2 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4491 | 3747 | 6 | 3 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4492 | 3748 | 6 | 4 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4493 | 3749 | 6 | 5 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4494 | 3750 | 6 | 6 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4495 | 3751 | 6 | 7 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4496 | 3752 | 6 | 8 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4497 | 3753 | 6 | 9 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4498 | 3754 | 6 | 10 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4499 | 3755 | 6 | 11 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4500 | 3756 | 6 | 12 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4501 | 3757 | 6 | 13 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4502 | 3758 | 6 | 14 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4503 | 3759 | 6 | 15 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4504 | 3760 | 6 | 16 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4505 | 3761 | 6 | 17 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4506 | 3762 | 6 | 18 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4507 | 3763 | 6 | 19 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4508 | 3764 | 6 | 20 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4509 | 3765 | 6 | 21 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4510 | 3766 | 6 | 22 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4511 | 3767 | 6 | 23 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4512 | 3768 | 6 | 24 | 157 | 43257 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4513 | 3769 | 6 | 1 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4514 | 3770 | 6 | 2 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4515 | 3771 | 6 | 3 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4516 | 3772 | 6 | 4 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4517 | 3773 | 6 | 5 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4518 | 3774 | 6 | 6 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4519 | 3775 | 6 | 7 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4520 | 3776 | 6 | 8 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4521 | 3777 | 6 | 9 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4522 | 3778 | 6 | 10 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4523 | 3779 | 6 | 11 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4524 | 3780 | 6 | 12 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4525 | 3781 | 6 | 13 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4526 | 3782 | 6 | 14 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4527 | 3783 | 6 | 15 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4528 | 3784 | 6 | 16 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4529 | 3785 | 6 | 17 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4530 | 3786 | 6 | 18 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4531 | 3787 | 6 | 19 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4532 | 3788 | 6 | 20 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4533 | 3789 | 6 | 21 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4534 | 3790 | 6 | 22 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4535 | 3791 | 6 | 23 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4536 | 3792 | 6 | 24 | 158 | 43258 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4537 | 3793 | 6 | 1 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4538 | 3794 | 6 | 2 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4539 | 3795 | 6 | 3 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4540 | 3796 | 6 | 4 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4541 | 3797 | 6 | 5 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4542 | 3798 | 6 | 6 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4543 | 3799 | 6 | 7 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4544 | 3800 | 6 | 8 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4545 | 3801 | 6 | 9 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4546 | 3802 | 6 | 10 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4547 | 3803 | 6 | 11 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4548 | 3804 | 6 | 12 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4549 | 3805 | 6 | 13 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4550 | 3806 | 6 | 14 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4551 | 3807 | 6 | 15 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4552 | 3808 | 6 | 16 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4553 | 3809 | 6 | 17 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4554 | 3810 | 6 | 18 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4555 | 3811 | 6 | 19 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4556 | 3812 | 6 | 20 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4557 | 3813 | 6 | 21 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4558 | 3814 | 6 | 22 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4559 | 3815 | 6 | 23 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4560 | 3816 | 6 | 24 | 159 | 43259 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4561 | 3817 | 6 | 1 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4562 | 3818 | 6 | 2 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4563 | 3819 | 6 | 3 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4564 | 3820 | 6 | 4 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4565 | 3821 | 6 | 5 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4566 | 3822 | 6 | 6 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4567 | 3823 | 6 | 7 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4568 | 3824 | 6 | 8 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4569 | 3825 | 6 | 9 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4570 | 3826 | 6 | 10 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4571 | 3827 | 6 | 11 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4572 | 3828 | 6 | 12 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4573 | 3829 | 6 | 13 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4574 | 3830 | 6 | 14 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4575 | 3831 | 6 | 15 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4576 | 3832 | 6 | 16 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4577 | 3833 | 6 | 17 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4578 | 3834 | 6 | 18 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4579 | 3835 | 6 | 19 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4580 | 3836 | 6 | 20 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4581 | 3837 | 6 | 21 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4582 | 3838 | 6 | 22 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4583 | 3839 | 6 | 23 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4584 | 3840 | 6 | 24 | 160 | 43260 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4585 | 3841 | 6 | 1 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4586 | 3842 | 6 | 2 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4587 | 3843 | 6 | 3 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4588 | 3844 | 6 | 4 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4589 | 3845 | 6 | 5 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4590 | 3846 | 6 | 6 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4591 | 3847 | 6 | 7 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4592 | 3848 | 6 | 8 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4593 | 3849 | 6 | 9 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4594 | 3850 | 6 | 10 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4595 | 3851 | 6 | 11 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4596 | 3852 | 6 | 12 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4597 | 3853 | 6 | 13 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4598 | 3854 | 6 | 14 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4599 | 3855 | 6 | 15 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4600 | 3856 | 6 | 16 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4601 | 3857 | 6 | 17 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4602 | 3858 | 6 | 18 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4603 | 3859 | 6 | 19 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4604 | 3860 | 6 | 20 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4605 | 3861 | 6 | 21 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4606 | 3862 | 6 | 22 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4607 | 3863 | 6 | 23 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4608 | 3864 | 6 | 24 | 161 | 43261 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4609 | 3865 | 6 | 1 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4610 | 3866 | 6 | 2 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4611 | 3867 | 6 | 3 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4612 | 3868 | 6 | 4 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4613 | 3869 | 6 | 5 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4614 | 3870 | 6 | 6 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4615 | 3871 | 6 | 7 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4616 | 3872 | 6 | 8 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4617 | 3873 | 6 | 9 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4618 | 3874 | 6 | 10 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4619 | 3875 | 6 | 11 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4620 | 3876 | 6 | 12 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4621 | 3877 | 6 | 13 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4622 | 3878 | 6 | 14 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4623 | 3879 | 6 | 15 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4624 | 3880 | 6 | 16 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4625 | 3881 | 6 | 17 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4626 | 3882 | 6 | 18 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4627 | 3883 | 6 | 19 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4628 | 3884 | 6 | 20 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4629 | 3885 | 6 | 21 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4630 | 3886 | 6 | 22 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4631 | 3887 | 6 | 23 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4632 | 3888 | 6 | 24 | 162 | 43262 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4633 | 3889 | 6 | 1 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4634 | 3890 | 6 | 2 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4635 | 3891 | 6 | 3 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4636 | 3892 | 6 | 4 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4637 | 3893 | 6 | 5 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4638 | 3894 | 6 | 6 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4639 | 3895 | 6 | 7 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4640 | 3896 | 6 | 8 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4641 | 3897 | 6 | 9 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4642 | 3898 | 6 | 10 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4643 | 3899 | 6 | 11 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4644 | 3900 | 6 | 12 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4645 | 3901 | 6 | 13 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4646 | 3902 | 6 | 14 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4647 | 3903 | 6 | 15 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4648 | 3904 | 6 | 16 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4649 | 3905 | 6 | 17 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4650 | 3906 | 6 | 18 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4651 | 3907 | 6 | 19 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4652 | 3908 | 6 | 20 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4653 | 3909 | 6 | 21 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4654 | 3910 | 6 | 22 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4655 | 3911 | 6 | 23 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4656 | 3912 | 6 | 24 | 163 | 43263 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4657 | 3913 | 6 | 1 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4658 | 3914 | 6 | 2 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4659 | 3915 | 6 | 3 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4660 | 3916 | 6 | 4 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4661 | 3917 | 6 | 5 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4662 | 3918 | 6 | 6 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4663 | 3919 | 6 | 7 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4664 | 3920 | 6 | 8 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4665 | 3921 | 6 | 9 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4666 | 3922 | 6 | 10 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4667 | 3923 | 6 | 11 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4668 | 3924 | 6 | 12 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4669 | 3925 | 6 | 13 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4670 | 3926 | 6 | 14 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4671 | 3927 | 6 | 15 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4672 | 3928 | 6 | 16 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4673 | 3929 | 6 | 17 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4674 | 3930 | 6 | 18 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4675 | 3931 | 6 | 19 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4676 | 3932 | 6 | 20 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4677 | 3933 | 6 | 21 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4678 | 3934 | 6 | 22 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4679 | 3935 | 6 | 23 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4680 | 3936 | 6 | 24 | 164 | 43264 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4681 | 3937 | 6 | 1 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4682 | 3938 | 6 | 2 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4683 | 3939 | 6 | 3 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4684 | 3940 | 6 | 4 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4685 | 3941 | 6 | 5 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4686 | 3942 | 6 | 6 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4687 | 3943 | 6 | 7 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4688 | 3944 | 6 | 8 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4689 | 3945 | 6 | 9 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4690 | 3946 | 6 | 10 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4691 | 3947 | 6 | 11 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4692 | 3948 | 6 | 12 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4693 | 3949 | 6 | 13 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4694 | 3950 | 6 | 14 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4695 | 3951 | 6 | 15 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4696 | 3952 | 6 | 16 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4697 | 3953 | 6 | 17 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4698 | 3954 | 6 | 18 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4699 | 3955 | 6 | 19 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4700 | 3956 | 6 | 20 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4701 | 3957 | 6 | 21 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4702 | 3958 | 6 | 22 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4703 | 3959 | 6 | 23 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4704 | 3960 | 6 | 24 | 165 | 43265 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4705 | 3961 | 6 | 1 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4706 | 3962 | 6 | 2 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4707 | 3963 | 6 | 3 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4708 | 3964 | 6 | 4 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4709 | 3965 | 6 | 5 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4710 | 3966 | 6 | 6 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4711 | 3967 | 6 | 7 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4712 | 3968 | 6 | 8 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4713 | 3969 | 6 | 9 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4714 | 3970 | 6 | 10 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4715 | 3971 | 6 | 11 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4716 | 3972 | 6 | 12 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4717 | 3973 | 6 | 13 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4718 | 3974 | 6 | 14 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4719 | 3975 | 6 | 15 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4720 | 3976 | 6 | 16 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4721 | 3977 | 6 | 17 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4722 | 3978 | 6 | 18 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4723 | 3979 | 6 | 19 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4724 | 3980 | 6 | 20 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4725 | 3981 | 6 | 21 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4726 | 3982 | 6 | 22 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4727 | 3983 | 6 | 23 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4728 | 3984 | 6 | 24 | 166 | 43266 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4729 | 3985 | 6 | 1 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4730 | 3986 | 6 | 2 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4731 | 3987 | 6 | 3 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4732 | 3988 | 6 | 4 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4733 | 3989 | 6 | 5 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4734 | 3990 | 6 | 6 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4735 | 3991 | 6 | 7 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4736 | 3992 | 6 | 8 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4737 | 3993 | 6 | 9 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4738 | 3994 | 6 | 10 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4739 | 3995 | 6 | 11 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4740 | 3996 | 6 | 12 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4741 | 3997 | 6 | 13 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4742 | 3998 | 6 | 14 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4743 | 3999 | 6 | 15 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4744 | 4000 | 6 | 16 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4745 | 4001 | 6 | 17 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4746 | 4002 | 6 | 18 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4747 | 4003 | 6 | 19 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4748 | 4004 | 6 | 20 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4749 | 4005 | 6 | 21 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4750 | 4006 | 6 | 22 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4751 | 4007 | 6 | 23 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4752 | 4008 | 6 | 24 | 167 | 43267 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4753 | 4009 | 6 | 1 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4754 | 4010 | 6 | 2 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4755 | 4011 | 6 | 3 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4756 | 4012 | 6 | 4 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4757 | 4013 | 6 | 5 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4758 | 4014 | 6 | 6 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4759 | 4015 | 6 | 7 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4760 | 4016 | 6 | 8 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4761 | 4017 | 6 | 9 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4762 | 4018 | 6 | 10 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4763 | 4019 | 6 | 11 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4764 | 4020 | 6 | 12 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4765 | 4021 | 6 | 13 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4766 | 4022 | 6 | 14 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4767 | 4023 | 6 | 15 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4768 | 4024 | 6 | 16 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4769 | 4025 | 6 | 17 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4770 | 4026 | 6 | 18 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4771 | 4027 | 6 | 19 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4772 | 4028 | 6 | 20 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4773 | 4029 | 6 | 21 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4774 | 4030 | 6 | 22 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4775 | 4031 | 6 | 23 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4776 | 4032 | 6 | 24 | 168 | 43268 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4777 | 4033 | 6 | 1 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4778 | 4034 | 6 | 2 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4779 | 4035 | 6 | 3 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4780 | 4036 | 6 | 4 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4781 | 4037 | 6 | 5 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4782 | 4038 | 6 | 6 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4783 | 4039 | 6 | 7 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4784 | 4040 | 6 | 8 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4785 | 4041 | 6 | 9 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4786 | 4042 | 6 | 10 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4787 | 4043 | 6 | 11 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4788 | 4044 | 6 | 12 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4789 | 4045 | 6 | 13 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4790 | 4046 | 6 | 14 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4791 | 4047 | 6 | 15 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4792 | 4048 | 6 | 16 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4793 | 4049 | 6 | 17 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4794 | 4050 | 6 | 18 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4795 | 4051 | 6 | 19 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4796 | 4052 | 6 | 20 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4797 | 4053 | 6 | 21 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4798 | 4054 | 6 | 22 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4799 | 4055 | 6 | 23 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4800 | 4056 | 6 | 24 | 169 | 43269 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4801 | 4057 | 6 | 1 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4802 | 4058 | 6 | 2 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4803 | 4059 | 6 | 3 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4804 | 4060 | 6 | 4 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4805 | 4061 | 6 | 5 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4806 | 4062 | 6 | 6 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4807 | 4063 | 6 | 7 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4808 | 4064 | 6 | 8 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4809 | 4065 | 6 | 9 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4810 | 4066 | 6 | 10 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4811 | 4067 | 6 | 11 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4812 | 4068 | 6 | 12 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4813 | 4069 | 6 | 13 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4814 | 4070 | 6 | 14 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4815 | 4071 | 6 | 15 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4816 | 4072 | 6 | 16 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4817 | 4073 | 6 | 17 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4818 | 4074 | 6 | 18 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4819 | 4075 | 6 | 19 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4820 | 4076 | 6 | 20 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4821 | 4077 | 6 | 21 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4822 | 4078 | 6 | 22 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4823 | 4079 | 6 | 23 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4824 | 4080 | 6 | 24 | 170 | 43270 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4825 | 4081 | 6 | 1 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4826 | 4082 | 6 | 2 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4827 | 4083 | 6 | 3 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4828 | 4084 | 6 | 4 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4829 | 4085 | 6 | 5 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4830 | 4086 | 6 | 6 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4831 | 4087 | 6 | 7 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4832 | 4088 | 6 | 8 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4833 | 4089 | 6 | 9 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4834 | 4090 | 6 | 10 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4835 | 4091 | 6 | 11 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4836 | 4092 | 6 | 12 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4837 | 4093 | 6 | 13 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4838 | 4094 | 6 | 14 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4839 | 4095 | 6 | 15 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4840 | 4096 | 6 | 16 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4841 | 4097 | 6 | 17 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4842 | 4098 | 6 | 18 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4843 | 4099 | 6 | 19 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4844 | 4100 | 6 | 20 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4845 | 4101 | 6 | 21 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4846 | 4102 | 6 | 22 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4847 | 4103 | 6 | 23 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4848 | 4104 | 6 | 24 | 171 | 43271 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4849 | 4105 | 6 | 1 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4850 | 4106 | 6 | 2 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4851 | 4107 | 6 | 3 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4852 | 4108 | 6 | 4 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4853 | 4109 | 6 | 5 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4854 | 4110 | 6 | 6 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4855 | 4111 | 6 | 7 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4856 | 4112 | 6 | 8 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4857 | 4113 | 6 | 9 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4858 | 4114 | 6 | 10 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4859 | 4115 | 6 | 11 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4860 | 4116 | 6 | 12 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4861 | 4117 | 6 | 13 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4862 | 4118 | 6 | 14 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4863 | 4119 | 6 | 15 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4864 | 4120 | 6 | 16 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4865 | 4121 | 6 | 17 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4866 | 4122 | 6 | 18 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4867 | 4123 | 6 | 19 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4868 | 4124 | 6 | 20 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4869 | 4125 | 6 | 21 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4870 | 4126 | 6 | 22 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4871 | 4127 | 6 | 23 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4872 | 4128 | 6 | 24 | 172 | 43272 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4873 | 4129 | 6 | 1 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4874 | 4130 | 6 | 2 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4875 | 4131 | 6 | 3 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4876 | 4132 | 6 | 4 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4877 | 4133 | 6 | 5 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4878 | 4134 | 6 | 6 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4879 | 4135 | 6 | 7 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4880 | 4136 | 6 | 8 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4881 | 4137 | 6 | 9 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4882 | 4138 | 6 | 10 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4883 | 4139 | 6 | 11 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4884 | 4140 | 6 | 12 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4885 | 4141 | 6 | 13 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4886 | 4142 | 6 | 14 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4887 | 4143 | 6 | 15 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4888 | 4144 | 6 | 16 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4889 | 4145 | 6 | 17 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4890 | 4146 | 6 | 18 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4891 | 4147 | 6 | 19 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4892 | 4148 | 6 | 20 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4893 | 4149 | 6 | 21 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4894 | 4150 | 6 | 22 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4895 | 4151 | 6 | 23 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4896 | 4152 | 6 | 24 | 173 | 43273 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4897 | 4153 | 6 | 1 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4898 | 4154 | 6 | 2 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4899 | 4155 | 6 | 3 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4900 | 4156 | 6 | 4 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4901 | 4157 | 6 | 5 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4902 | 4158 | 6 | 6 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4903 | 4159 | 6 | 7 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4904 | 4160 | 6 | 8 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4905 | 4161 | 6 | 9 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4906 | 4162 | 6 | 10 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4907 | 4163 | 6 | 11 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4908 | 4164 | 6 | 12 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4909 | 4165 | 6 | 13 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4910 | 4166 | 6 | 14 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4911 | 4167 | 6 | 15 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4912 | 4168 | 6 | 16 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4913 | 4169 | 6 | 17 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4914 | 4170 | 6 | 18 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4915 | 4171 | 6 | 19 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4916 | 4172 | 6 | 20 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4917 | 4173 | 6 | 21 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4918 | 4174 | 6 | 22 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4919 | 4175 | 6 | 23 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4920 | 4176 | 6 | 24 | 174 | 43274 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4921 | 4177 | 6 | 1 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4922 | 4178 | 6 | 2 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4923 | 4179 | 6 | 3 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4924 | 4180 | 6 | 4 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4925 | 4181 | 6 | 5 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4926 | 4182 | 6 | 6 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4927 | 4183 | 6 | 7 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4928 | 4184 | 6 | 8 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4929 | 4185 | 6 | 9 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4930 | 4186 | 6 | 10 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4931 | 4187 | 6 | 11 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4932 | 4188 | 6 | 12 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4933 | 4189 | 6 | 13 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4934 | 4190 | 6 | 14 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4935 | 4191 | 6 | 15 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4936 | 4192 | 6 | 16 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4937 | 4193 | 6 | 17 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4938 | 4194 | 6 | 18 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4939 | 4195 | 6 | 19 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4940 | 4196 | 6 | 20 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4941 | 4197 | 6 | 21 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4942 | 4198 | 6 | 22 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4943 | 4199 | 6 | 23 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4944 | 4200 | 6 | 24 | 175 | 43275 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4945 | 4201 | 6 | 1 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4946 | 4202 | 6 | 2 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4947 | 4203 | 6 | 3 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4948 | 4204 | 6 | 4 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4949 | 4205 | 6 | 5 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4950 | 4206 | 6 | 6 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4951 | 4207 | 6 | 7 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4952 | 4208 | 6 | 8 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4953 | 4209 | 6 | 9 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4954 | 4210 | 6 | 10 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4955 | 4211 | 6 | 11 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4956 | 4212 | 6 | 12 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4957 | 4213 | 6 | 13 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4958 | 4214 | 6 | 14 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4959 | 4215 | 6 | 15 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4960 | 4216 | 6 | 16 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4961 | 4217 | 6 | 17 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4962 | 4218 | 6 | 18 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4963 | 4219 | 6 | 19 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4964 | 4220 | 6 | 20 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4965 | 4221 | 6 | 21 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4966 | 4222 | 6 | 22 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4967 | 4223 | 6 | 23 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4968 | 4224 | 6 | 24 | 176 | 43276 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4969 | 4225 | 6 | 1 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4970 | 4226 | 6 | 2 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4971 | 4227 | 6 | 3 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4972 | 4228 | 6 | 4 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4973 | 4229 | 6 | 5 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4974 | 4230 | 6 | 6 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4975 | 4231 | 6 | 7 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4976 | 4232 | 6 | 8 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4977 | 4233 | 6 | 9 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4978 | 4234 | 6 | 10 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4979 | 4235 | 6 | 11 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4980 | 4236 | 6 | 12 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4981 | 4237 | 6 | 13 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4982 | 4238 | 6 | 14 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4983 | 4239 | 6 | 15 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4984 | 4240 | 6 | 16 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4985 | 4241 | 6 | 17 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4986 | 4242 | 6 | 18 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4987 | 4243 | 6 | 19 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4988 | 4244 | 6 | 20 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4989 | 4245 | 6 | 21 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4990 | 4246 | 6 | 22 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4991 | 4247 | 6 | 23 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4992 | 4248 | 6 | 24 | 177 | 43277 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4993 | 4249 | 6 | 1 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4994 | 4250 | 6 | 2 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4995 | 4251 | 6 | 3 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4996 | 4252 | 6 | 4 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4997 | 4253 | 6 | 5 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4998 | 4254 | 6 | 6 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 4999 | 4255 | 6 | 7 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5000 | 4256 | 6 | 8 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5001 | 4257 | 6 | 9 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5002 | 4258 | 6 | 10 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5003 | 4259 | 6 | 11 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5004 | 4260 | 6 | 12 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5005 | 4261 | 6 | 13 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5006 | 4262 | 6 | 14 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5007 | 4263 | 6 | 15 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5008 | 4264 | 6 | 16 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5009 | 4265 | 6 | 17 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5010 | 4266 | 6 | 18 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5011 | 4267 | 6 | 19 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5012 | 4268 | 6 | 20 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5013 | 4269 | 6 | 21 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5014 | 4270 | 6 | 22 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5015 | 4271 | 6 | 23 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5016 | 4272 | 6 | 24 | 178 | 43278 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5017 | 4273 | 6 | 1 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5018 | 4274 | 6 | 2 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5019 | 4275 | 6 | 3 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5020 | 4276 | 6 | 4 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5021 | 4277 | 6 | 5 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5022 | 4278 | 6 | 6 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5023 | 4279 | 6 | 7 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5024 | 4280 | 6 | 8 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5025 | 4281 | 6 | 9 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5026 | 4282 | 6 | 10 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5027 | 4283 | 6 | 11 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5028 | 4284 | 6 | 12 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5029 | 4285 | 6 | 13 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5030 | 4286 | 6 | 14 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5031 | 4287 | 6 | 15 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5032 | 4288 | 6 | 16 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5033 | 4289 | 6 | 17 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5034 | 4290 | 6 | 18 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5035 | 4291 | 6 | 19 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5036 | 4292 | 6 | 20 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5037 | 4293 | 6 | 21 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5038 | 4294 | 6 | 22 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5039 | 4295 | 6 | 23 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5040 | 4296 | 6 | 24 | 179 | 43279 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5041 | 4297 | 6 | 1 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5042 | 4298 | 6 | 2 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5043 | 4299 | 6 | 3 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5044 | 4300 | 6 | 4 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5045 | 4301 | 6 | 5 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5046 | 4302 | 6 | 6 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5047 | 4303 | 6 | 7 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5048 | 4304 | 6 | 8 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5049 | 4305 | 6 | 9 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5050 | 4306 | 6 | 10 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5051 | 4307 | 6 | 11 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5052 | 4308 | 6 | 12 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5053 | 4309 | 6 | 13 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5054 | 4310 | 6 | 14 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5055 | 4311 | 6 | 15 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5056 | 4312 | 6 | 16 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5057 | 4313 | 6 | 17 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5058 | 4314 | 6 | 18 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5059 | 4315 | 6 | 19 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5060 | 4316 | 6 | 20 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5061 | 4317 | 6 | 21 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5062 | 4318 | 6 | 22 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5063 | 4319 | 6 | 23 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5064 | 4320 | 6 | 24 | 180 | 43280 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5065 | 4321 | 6 | 1 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5066 | 4322 | 6 | 2 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5067 | 4323 | 6 | 3 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5068 | 4324 | 6 | 4 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5069 | 4325 | 6 | 5 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5070 | 4326 | 6 | 6 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5071 | 4327 | 6 | 7 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5072 | 4328 | 6 | 8 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5073 | 4329 | 6 | 9 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5074 | 4330 | 6 | 10 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5075 | 4331 | 6 | 11 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5076 | 4332 | 6 | 12 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5077 | 4333 | 6 | 13 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5078 | 4334 | 6 | 14 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5079 | 4335 | 6 | 15 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5080 | 4336 | 6 | 16 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5081 | 4337 | 6 | 17 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5082 | 4338 | 6 | 18 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5083 | 4339 | 6 | 19 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5084 | 4340 | 6 | 20 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5085 | 4341 | 6 | 21 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5086 | 4342 | 6 | 22 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5087 | 4343 | 6 | 23 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5088 | 4344 | 6 | 24 | 181 | 43281 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5089 | 4345 | 7 | 1 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5090 | 4346 | 7 | 2 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5091 | 4347 | 7 | 3 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5092 | 4348 | 7 | 4 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5093 | 4349 | 7 | 5 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5094 | 4350 | 7 | 6 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5095 | 4351 | 7 | 7 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5096 | 4352 | 7 | 8 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5097 | 4353 | 7 | 9 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5098 | 4354 | 7 | 10 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5099 | 4355 | 7 | 11 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5100 | 4356 | 7 | 12 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5101 | 4357 | 7 | 13 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5102 | 4358 | 7 | 14 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5103 | 4359 | 7 | 15 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5104 | 4360 | 7 | 16 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5105 | 4361 | 7 | 17 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5106 | 4362 | 7 | 18 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5107 | 4363 | 7 | 19 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5108 | 4364 | 7 | 20 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5109 | 4365 | 7 | 21 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5110 | 4366 | 7 | 22 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5111 | 4367 | 7 | 23 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5112 | 4368 | 7 | 24 | 182 | 43282 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5113 | 4369 | 7 | 1 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5114 | 4370 | 7 | 2 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5115 | 4371 | 7 | 3 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5116 | 4372 | 7 | 4 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5117 | 4373 | 7 | 5 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5118 | 4374 | 7 | 6 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5119 | 4375 | 7 | 7 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5120 | 4376 | 7 | 8 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5121 | 4377 | 7 | 9 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5122 | 4378 | 7 | 10 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5123 | 4379 | 7 | 11 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5124 | 4380 | 7 | 12 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5125 | 4381 | 7 | 13 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5126 | 4382 | 7 | 14 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5127 | 4383 | 7 | 15 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5128 | 4384 | 7 | 16 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5129 | 4385 | 7 | 17 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5130 | 4386 | 7 | 18 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5131 | 4387 | 7 | 19 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5132 | 4388 | 7 | 20 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5133 | 4389 | 7 | 21 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5134 | 4390 | 7 | 22 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5135 | 4391 | 7 | 23 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5136 | 4392 | 7 | 24 | 183 | 43283 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5137 | 4393 | 7 | 1 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5138 | 4394 | 7 | 2 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5139 | 4395 | 7 | 3 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5140 | 4396 | 7 | 4 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5141 | 4397 | 7 | 5 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5142 | 4398 | 7 | 6 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5143 | 4399 | 7 | 7 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5144 | 4400 | 7 | 8 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5145 | 4401 | 7 | 9 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5146 | 4402 | 7 | 10 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5147 | 4403 | 7 | 11 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5148 | 4404 | 7 | 12 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5149 | 4405 | 7 | 13 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5150 | 4406 | 7 | 14 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5151 | 4407 | 7 | 15 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5152 | 4408 | 7 | 16 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5153 | 4409 | 7 | 17 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5154 | 4410 | 7 | 18 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5155 | 4411 | 7 | 19 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5156 | 4412 | 7 | 20 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5157 | 4413 | 7 | 21 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5158 | 4414 | 7 | 22 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5159 | 4415 | 7 | 23 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5160 | 4416 | 7 | 24 | 184 | 43284 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5161 | 4417 | 7 | 1 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5162 | 4418 | 7 | 2 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5163 | 4419 | 7 | 3 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5164 | 4420 | 7 | 4 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5165 | 4421 | 7 | 5 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5166 | 4422 | 7 | 6 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5167 | 4423 | 7 | 7 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5168 | 4424 | 7 | 8 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5169 | 4425 | 7 | 9 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5170 | 4426 | 7 | 10 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5171 | 4427 | 7 | 11 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5172 | 4428 | 7 | 12 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5173 | 4429 | 7 | 13 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5174 | 4430 | 7 | 14 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5175 | 4431 | 7 | 15 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5176 | 4432 | 7 | 16 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5177 | 4433 | 7 | 17 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5178 | 4434 | 7 | 18 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5179 | 4435 | 7 | 19 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5180 | 4436 | 7 | 20 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5181 | 4437 | 7 | 21 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5182 | 4438 | 7 | 22 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5183 | 4439 | 7 | 23 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5184 | 4440 | 7 | 24 | 185 | 43285 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5185 | 4441 | 7 | 1 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5186 | 4442 | 7 | 2 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5187 | 4443 | 7 | 3 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5188 | 4444 | 7 | 4 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5189 | 4445 | 7 | 5 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5190 | 4446 | 7 | 6 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5191 | 4447 | 7 | 7 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5192 | 4448 | 7 | 8 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5193 | 4449 | 7 | 9 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5194 | 4450 | 7 | 10 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5195 | 4451 | 7 | 11 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5196 | 4452 | 7 | 12 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5197 | 4453 | 7 | 13 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5198 | 4454 | 7 | 14 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5199 | 4455 | 7 | 15 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5200 | 4456 | 7 | 16 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5201 | 4457 | 7 | 17 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5202 | 4458 | 7 | 18 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5203 | 4459 | 7 | 19 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5204 | 4460 | 7 | 20 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5205 | 4461 | 7 | 21 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5206 | 4462 | 7 | 22 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5207 | 4463 | 7 | 23 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5208 | 4464 | 7 | 24 | 186 | 43286 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5209 | 4465 | 7 | 1 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5210 | 4466 | 7 | 2 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5211 | 4467 | 7 | 3 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5212 | 4468 | 7 | 4 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5213 | 4469 | 7 | 5 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5214 | 4470 | 7 | 6 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5215 | 4471 | 7 | 7 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5216 | 4472 | 7 | 8 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5217 | 4473 | 7 | 9 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5218 | 4474 | 7 | 10 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5219 | 4475 | 7 | 11 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5220 | 4476 | 7 | 12 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5221 | 4477 | 7 | 13 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5222 | 4478 | 7 | 14 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5223 | 4479 | 7 | 15 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5224 | 4480 | 7 | 16 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5225 | 4481 | 7 | 17 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5226 | 4482 | 7 | 18 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5227 | 4483 | 7 | 19 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5228 | 4484 | 7 | 20 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5229 | 4485 | 7 | 21 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5230 | 4486 | 7 | 22 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5231 | 4487 | 7 | 23 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5232 | 4488 | 7 | 24 | 187 | 43287 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5233 | 4489 | 7 | 1 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5234 | 4490 | 7 | 2 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5235 | 4491 | 7 | 3 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5236 | 4492 | 7 | 4 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5237 | 4493 | 7 | 5 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5238 | 4494 | 7 | 6 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5239 | 4495 | 7 | 7 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5240 | 4496 | 7 | 8 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5241 | 4497 | 7 | 9 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5242 | 4498 | 7 | 10 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5243 | 4499 | 7 | 11 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5244 | 4500 | 7 | 12 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5245 | 4501 | 7 | 13 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5246 | 4502 | 7 | 14 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5247 | 4503 | 7 | 15 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5248 | 4504 | 7 | 16 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5249 | 4505 | 7 | 17 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5250 | 4506 | 7 | 18 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5251 | 4507 | 7 | 19 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5252 | 4508 | 7 | 20 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5253 | 4509 | 7 | 21 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5254 | 4510 | 7 | 22 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5255 | 4511 | 7 | 23 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5256 | 4512 | 7 | 24 | 188 | 43288 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5257 | 4513 | 7 | 1 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5258 | 4514 | 7 | 2 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5259 | 4515 | 7 | 3 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5260 | 4516 | 7 | 4 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5261 | 4517 | 7 | 5 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5262 | 4518 | 7 | 6 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5263 | 4519 | 7 | 7 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5264 | 4520 | 7 | 8 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5265 | 4521 | 7 | 9 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5266 | 4522 | 7 | 10 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5267 | 4523 | 7 | 11 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5268 | 4524 | 7 | 12 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5269 | 4525 | 7 | 13 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5270 | 4526 | 7 | 14 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5271 | 4527 | 7 | 15 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5272 | 4528 | 7 | 16 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5273 | 4529 | 7 | 17 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5274 | 4530 | 7 | 18 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5275 | 4531 | 7 | 19 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5276 | 4532 | 7 | 20 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5277 | 4533 | 7 | 21 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5278 | 4534 | 7 | 22 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5279 | 4535 | 7 | 23 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5280 | 4536 | 7 | 24 | 189 | 43289 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5281 | 4537 | 7 | 1 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5282 | 4538 | 7 | 2 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5283 | 4539 | 7 | 3 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5284 | 4540 | 7 | 4 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5285 | 4541 | 7 | 5 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5286 | 4542 | 7 | 6 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5287 | 4543 | 7 | 7 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5288 | 4544 | 7 | 8 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5289 | 4545 | 7 | 9 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5290 | 4546 | 7 | 10 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5291 | 4547 | 7 | 11 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5292 | 4548 | 7 | 12 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5293 | 4549 | 7 | 13 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5294 | 4550 | 7 | 14 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5295 | 4551 | 7 | 15 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5296 | 4552 | 7 | 16 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5297 | 4553 | 7 | 17 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5298 | 4554 | 7 | 18 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5299 | 4555 | 7 | 19 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5300 | 4556 | 7 | 20 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5301 | 4557 | 7 | 21 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5302 | 4558 | 7 | 22 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5303 | 4559 | 7 | 23 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5304 | 4560 | 7 | 24 | 190 | 43290 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5305 | 4561 | 7 | 1 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5306 | 4562 | 7 | 2 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5307 | 4563 | 7 | 3 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5308 | 4564 | 7 | 4 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5309 | 4565 | 7 | 5 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5310 | 4566 | 7 | 6 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5311 | 4567 | 7 | 7 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5312 | 4568 | 7 | 8 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5313 | 4569 | 7 | 9 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5314 | 4570 | 7 | 10 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5315 | 4571 | 7 | 11 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5316 | 4572 | 7 | 12 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5317 | 4573 | 7 | 13 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5318 | 4574 | 7 | 14 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5319 | 4575 | 7 | 15 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5320 | 4576 | 7 | 16 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5321 | 4577 | 7 | 17 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5322 | 4578 | 7 | 18 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5323 | 4579 | 7 | 19 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5324 | 4580 | 7 | 20 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5325 | 4581 | 7 | 21 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5326 | 4582 | 7 | 22 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5327 | 4583 | 7 | 23 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5328 | 4584 | 7 | 24 | 191 | 43291 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5329 | 4585 | 7 | 1 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5330 | 4586 | 7 | 2 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5331 | 4587 | 7 | 3 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5332 | 4588 | 7 | 4 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5333 | 4589 | 7 | 5 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5334 | 4590 | 7 | 6 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5335 | 4591 | 7 | 7 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5336 | 4592 | 7 | 8 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5337 | 4593 | 7 | 9 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5338 | 4594 | 7 | 10 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5339 | 4595 | 7 | 11 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5340 | 4596 | 7 | 12 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5341 | 4597 | 7 | 13 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5342 | 4598 | 7 | 14 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5343 | 4599 | 7 | 15 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5344 | 4600 | 7 | 16 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5345 | 4601 | 7 | 17 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5346 | 4602 | 7 | 18 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5347 | 4603 | 7 | 19 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5348 | 4604 | 7 | 20 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5349 | 4605 | 7 | 21 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5350 | 4606 | 7 | 22 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5351 | 4607 | 7 | 23 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5352 | 4608 | 7 | 24 | 192 | 43292 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5353 | 4609 | 7 | 1 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5354 | 4610 | 7 | 2 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5355 | 4611 | 7 | 3 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5356 | 4612 | 7 | 4 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5357 | 4613 | 7 | 5 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5358 | 4614 | 7 | 6 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5359 | 4615 | 7 | 7 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5360 | 4616 | 7 | 8 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5361 | 4617 | 7 | 9 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5362 | 4618 | 7 | 10 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5363 | 4619 | 7 | 11 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5364 | 4620 | 7 | 12 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5365 | 4621 | 7 | 13 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5366 | 4622 | 7 | 14 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5367 | 4623 | 7 | 15 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5368 | 4624 | 7 | 16 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5369 | 4625 | 7 | 17 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5370 | 4626 | 7 | 18 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5371 | 4627 | 7 | 19 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5372 | 4628 | 7 | 20 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5373 | 4629 | 7 | 21 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5374 | 4630 | 7 | 22 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5375 | 4631 | 7 | 23 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5376 | 4632 | 7 | 24 | 193 | 43293 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5377 | 4633 | 7 | 1 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5378 | 4634 | 7 | 2 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5379 | 4635 | 7 | 3 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5380 | 4636 | 7 | 4 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5381 | 4637 | 7 | 5 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5382 | 4638 | 7 | 6 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5383 | 4639 | 7 | 7 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5384 | 4640 | 7 | 8 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5385 | 4641 | 7 | 9 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5386 | 4642 | 7 | 10 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5387 | 4643 | 7 | 11 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5388 | 4644 | 7 | 12 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5389 | 4645 | 7 | 13 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5390 | 4646 | 7 | 14 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5391 | 4647 | 7 | 15 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5392 | 4648 | 7 | 16 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5393 | 4649 | 7 | 17 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5394 | 4650 | 7 | 18 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5395 | 4651 | 7 | 19 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5396 | 4652 | 7 | 20 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5397 | 4653 | 7 | 21 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5398 | 4654 | 7 | 22 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5399 | 4655 | 7 | 23 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5400 | 4656 | 7 | 24 | 194 | 43294 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5401 | 4657 | 7 | 1 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5402 | 4658 | 7 | 2 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5403 | 4659 | 7 | 3 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5404 | 4660 | 7 | 4 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5405 | 4661 | 7 | 5 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5406 | 4662 | 7 | 6 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5407 | 4663 | 7 | 7 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5408 | 4664 | 7 | 8 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5409 | 4665 | 7 | 9 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5410 | 4666 | 7 | 10 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5411 | 4667 | 7 | 11 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5412 | 4668 | 7 | 12 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5413 | 4669 | 7 | 13 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5414 | 4670 | 7 | 14 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5415 | 4671 | 7 | 15 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5416 | 4672 | 7 | 16 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5417 | 4673 | 7 | 17 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5418 | 4674 | 7 | 18 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5419 | 4675 | 7 | 19 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5420 | 4676 | 7 | 20 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5421 | 4677 | 7 | 21 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5422 | 4678 | 7 | 22 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5423 | 4679 | 7 | 23 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5424 | 4680 | 7 | 24 | 195 | 43295 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5425 | 4681 | 7 | 1 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5426 | 4682 | 7 | 2 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5427 | 4683 | 7 | 3 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5428 | 4684 | 7 | 4 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5429 | 4685 | 7 | 5 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5430 | 4686 | 7 | 6 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5431 | 4687 | 7 | 7 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5432 | 4688 | 7 | 8 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5433 | 4689 | 7 | 9 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5434 | 4690 | 7 | 10 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5435 | 4691 | 7 | 11 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5436 | 4692 | 7 | 12 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5437 | 4693 | 7 | 13 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5438 | 4694 | 7 | 14 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5439 | 4695 | 7 | 15 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5440 | 4696 | 7 | 16 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5441 | 4697 | 7 | 17 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5442 | 4698 | 7 | 18 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5443 | 4699 | 7 | 19 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5444 | 4700 | 7 | 20 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5445 | 4701 | 7 | 21 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5446 | 4702 | 7 | 22 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5447 | 4703 | 7 | 23 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5448 | 4704 | 7 | 24 | 196 | 43296 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5449 | 4705 | 7 | 1 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5450 | 4706 | 7 | 2 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5451 | 4707 | 7 | 3 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5452 | 4708 | 7 | 4 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5453 | 4709 | 7 | 5 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5454 | 4710 | 7 | 6 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5455 | 4711 | 7 | 7 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5456 | 4712 | 7 | 8 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5457 | 4713 | 7 | 9 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5458 | 4714 | 7 | 10 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5459 | 4715 | 7 | 11 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5460 | 4716 | 7 | 12 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5461 | 4717 | 7 | 13 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5462 | 4718 | 7 | 14 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5463 | 4719 | 7 | 15 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5464 | 4720 | 7 | 16 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5465 | 4721 | 7 | 17 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5466 | 4722 | 7 | 18 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5467 | 4723 | 7 | 19 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5468 | 4724 | 7 | 20 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5469 | 4725 | 7 | 21 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5470 | 4726 | 7 | 22 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5471 | 4727 | 7 | 23 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5472 | 4728 | 7 | 24 | 197 | 43297 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5473 | 4729 | 7 | 1 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5474 | 4730 | 7 | 2 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5475 | 4731 | 7 | 3 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5476 | 4732 | 7 | 4 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5477 | 4733 | 7 | 5 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5478 | 4734 | 7 | 6 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5479 | 4735 | 7 | 7 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5480 | 4736 | 7 | 8 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5481 | 4737 | 7 | 9 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5482 | 4738 | 7 | 10 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5483 | 4739 | 7 | 11 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5484 | 4740 | 7 | 12 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5485 | 4741 | 7 | 13 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5486 | 4742 | 7 | 14 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5487 | 4743 | 7 | 15 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5488 | 4744 | 7 | 16 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5489 | 4745 | 7 | 17 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5490 | 4746 | 7 | 18 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5491 | 4747 | 7 | 19 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5492 | 4748 | 7 | 20 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5493 | 4749 | 7 | 21 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5494 | 4750 | 7 | 22 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5495 | 4751 | 7 | 23 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5496 | 4752 | 7 | 24 | 198 | 43298 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5497 | 4753 | 7 | 1 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5498 | 4754 | 7 | 2 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5499 | 4755 | 7 | 3 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5500 | 4756 | 7 | 4 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5501 | 4757 | 7 | 5 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5502 | 4758 | 7 | 6 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5503 | 4759 | 7 | 7 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5504 | 4760 | 7 | 8 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5505 | 4761 | 7 | 9 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5506 | 4762 | 7 | 10 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5507 | 4763 | 7 | 11 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5508 | 4764 | 7 | 12 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5509 | 4765 | 7 | 13 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5510 | 4766 | 7 | 14 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5511 | 4767 | 7 | 15 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5512 | 4768 | 7 | 16 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5513 | 4769 | 7 | 17 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5514 | 4770 | 7 | 18 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5515 | 4771 | 7 | 19 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5516 | 4772 | 7 | 20 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5517 | 4773 | 7 | 21 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5518 | 4774 | 7 | 22 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5519 | 4775 | 7 | 23 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5520 | 4776 | 7 | 24 | 199 | 43299 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5521 | 4777 | 7 | 1 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5522 | 4778 | 7 | 2 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5523 | 4779 | 7 | 3 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5524 | 4780 | 7 | 4 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5525 | 4781 | 7 | 5 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5526 | 4782 | 7 | 6 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5527 | 4783 | 7 | 7 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5528 | 4784 | 7 | 8 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5529 | 4785 | 7 | 9 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5530 | 4786 | 7 | 10 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5531 | 4787 | 7 | 11 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5532 | 4788 | 7 | 12 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5533 | 4789 | 7 | 13 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5534 | 4790 | 7 | 14 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5535 | 4791 | 7 | 15 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5536 | 4792 | 7 | 16 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5537 | 4793 | 7 | 17 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5538 | 4794 | 7 | 18 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5539 | 4795 | 7 | 19 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5540 | 4796 | 7 | 20 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5541 | 4797 | 7 | 21 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5542 | 4798 | 7 | 22 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5543 | 4799 | 7 | 23 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5544 | 4800 | 7 | 24 | 200 | 43300 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5545 | 4801 | 7 | 1 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5546 | 4802 | 7 | 2 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5547 | 4803 | 7 | 3 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5548 | 4804 | 7 | 4 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5549 | 4805 | 7 | 5 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5550 | 4806 | 7 | 6 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5551 | 4807 | 7 | 7 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5552 | 4808 | 7 | 8 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5553 | 4809 | 7 | 9 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5554 | 4810 | 7 | 10 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5555 | 4811 | 7 | 11 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5556 | 4812 | 7 | 12 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5557 | 4813 | 7 | 13 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5558 | 4814 | 7 | 14 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5559 | 4815 | 7 | 15 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5560 | 4816 | 7 | 16 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5561 | 4817 | 7 | 17 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5562 | 4818 | 7 | 18 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5563 | 4819 | 7 | 19 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5564 | 4820 | 7 | 20 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5565 | 4821 | 7 | 21 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5566 | 4822 | 7 | 22 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5567 | 4823 | 7 | 23 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5568 | 4824 | 7 | 24 | 201 | 43301 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5569 | 4825 | 7 | 1 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5570 | 4826 | 7 | 2 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5571 | 4827 | 7 | 3 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5572 | 4828 | 7 | 4 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5573 | 4829 | 7 | 5 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5574 | 4830 | 7 | 6 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5575 | 4831 | 7 | 7 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5576 | 4832 | 7 | 8 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5577 | 4833 | 7 | 9 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5578 | 4834 | 7 | 10 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5579 | 4835 | 7 | 11 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5580 | 4836 | 7 | 12 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5581 | 4837 | 7 | 13 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5582 | 4838 | 7 | 14 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5583 | 4839 | 7 | 15 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5584 | 4840 | 7 | 16 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5585 | 4841 | 7 | 17 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5586 | 4842 | 7 | 18 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5587 | 4843 | 7 | 19 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5588 | 4844 | 7 | 20 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5589 | 4845 | 7 | 21 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5590 | 4846 | 7 | 22 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5591 | 4847 | 7 | 23 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5592 | 4848 | 7 | 24 | 202 | 43302 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5593 | 4849 | 7 | 1 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5594 | 4850 | 7 | 2 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5595 | 4851 | 7 | 3 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5596 | 4852 | 7 | 4 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5597 | 4853 | 7 | 5 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5598 | 4854 | 7 | 6 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5599 | 4855 | 7 | 7 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5600 | 4856 | 7 | 8 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5601 | 4857 | 7 | 9 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5602 | 4858 | 7 | 10 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5603 | 4859 | 7 | 11 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5604 | 4860 | 7 | 12 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5605 | 4861 | 7 | 13 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5606 | 4862 | 7 | 14 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5607 | 4863 | 7 | 15 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5608 | 4864 | 7 | 16 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5609 | 4865 | 7 | 17 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5610 | 4866 | 7 | 18 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5611 | 4867 | 7 | 19 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5612 | 4868 | 7 | 20 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5613 | 4869 | 7 | 21 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5614 | 4870 | 7 | 22 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5615 | 4871 | 7 | 23 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5616 | 4872 | 7 | 24 | 203 | 43303 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5617 | 4873 | 7 | 1 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5618 | 4874 | 7 | 2 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5619 | 4875 | 7 | 3 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5620 | 4876 | 7 | 4 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5621 | 4877 | 7 | 5 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5622 | 4878 | 7 | 6 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5623 | 4879 | 7 | 7 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5624 | 4880 | 7 | 8 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5625 | 4881 | 7 | 9 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5626 | 4882 | 7 | 10 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5627 | 4883 | 7 | 11 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5628 | 4884 | 7 | 12 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5629 | 4885 | 7 | 13 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5630 | 4886 | 7 | 14 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5631 | 4887 | 7 | 15 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5632 | 4888 | 7 | 16 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5633 | 4889 | 7 | 17 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5634 | 4890 | 7 | 18 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5635 | 4891 | 7 | 19 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5636 | 4892 | 7 | 20 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5637 | 4893 | 7 | 21 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5638 | 4894 | 7 | 22 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5639 | 4895 | 7 | 23 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5640 | 4896 | 7 | 24 | 204 | 43304 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5641 | 4897 | 7 | 1 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5642 | 4898 | 7 | 2 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5643 | 4899 | 7 | 3 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5644 | 4900 | 7 | 4 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5645 | 4901 | 7 | 5 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5646 | 4902 | 7 | 6 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5647 | 4903 | 7 | 7 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5648 | 4904 | 7 | 8 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5649 | 4905 | 7 | 9 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5650 | 4906 | 7 | 10 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5651 | 4907 | 7 | 11 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5652 | 4908 | 7 | 12 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5653 | 4909 | 7 | 13 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5654 | 4910 | 7 | 14 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5655 | 4911 | 7 | 15 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5656 | 4912 | 7 | 16 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5657 | 4913 | 7 | 17 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5658 | 4914 | 7 | 18 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5659 | 4915 | 7 | 19 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5660 | 4916 | 7 | 20 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5661 | 4917 | 7 | 21 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5662 | 4918 | 7 | 22 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5663 | 4919 | 7 | 23 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5664 | 4920 | 7 | 24 | 205 | 43305 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5665 | 4921 | 7 | 1 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5666 | 4922 | 7 | 2 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5667 | 4923 | 7 | 3 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5668 | 4924 | 7 | 4 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5669 | 4925 | 7 | 5 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5670 | 4926 | 7 | 6 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5671 | 4927 | 7 | 7 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5672 | 4928 | 7 | 8 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5673 | 4929 | 7 | 9 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5674 | 4930 | 7 | 10 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5675 | 4931 | 7 | 11 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5676 | 4932 | 7 | 12 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5677 | 4933 | 7 | 13 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5678 | 4934 | 7 | 14 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5679 | 4935 | 7 | 15 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5680 | 4936 | 7 | 16 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5681 | 4937 | 7 | 17 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5682 | 4938 | 7 | 18 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5683 | 4939 | 7 | 19 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5684 | 4940 | 7 | 20 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5685 | 4941 | 7 | 21 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5686 | 4942 | 7 | 22 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5687 | 4943 | 7 | 23 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5688 | 4944 | 7 | 24 | 206 | 43306 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5689 | 4945 | 7 | 1 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5690 | 4946 | 7 | 2 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5691 | 4947 | 7 | 3 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5692 | 4948 | 7 | 4 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5693 | 4949 | 7 | 5 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5694 | 4950 | 7 | 6 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5695 | 4951 | 7 | 7 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5696 | 4952 | 7 | 8 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5697 | 4953 | 7 | 9 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5698 | 4954 | 7 | 10 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5699 | 4955 | 7 | 11 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5700 | 4956 | 7 | 12 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5701 | 4957 | 7 | 13 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5702 | 4958 | 7 | 14 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5703 | 4959 | 7 | 15 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5704 | 4960 | 7 | 16 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5705 | 4961 | 7 | 17 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5706 | 4962 | 7 | 18 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5707 | 4963 | 7 | 19 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5708 | 4964 | 7 | 20 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5709 | 4965 | 7 | 21 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5710 | 4966 | 7 | 22 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5711 | 4967 | 7 | 23 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5712 | 4968 | 7 | 24 | 207 | 43307 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5713 | 4969 | 7 | 1 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5714 | 4970 | 7 | 2 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5715 | 4971 | 7 | 3 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5716 | 4972 | 7 | 4 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5717 | 4973 | 7 | 5 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5718 | 4974 | 7 | 6 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5719 | 4975 | 7 | 7 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5720 | 4976 | 7 | 8 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5721 | 4977 | 7 | 9 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5722 | 4978 | 7 | 10 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5723 | 4979 | 7 | 11 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5724 | 4980 | 7 | 12 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5725 | 4981 | 7 | 13 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5726 | 4982 | 7 | 14 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5727 | 4983 | 7 | 15 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5728 | 4984 | 7 | 16 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5729 | 4985 | 7 | 17 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5730 | 4986 | 7 | 18 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5731 | 4987 | 7 | 19 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5732 | 4988 | 7 | 20 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5733 | 4989 | 7 | 21 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5734 | 4990 | 7 | 22 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5735 | 4991 | 7 | 23 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5736 | 4992 | 7 | 24 | 208 | 43308 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5737 | 4993 | 7 | 1 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5738 | 4994 | 7 | 2 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5739 | 4995 | 7 | 3 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5740 | 4996 | 7 | 4 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5741 | 4997 | 7 | 5 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5742 | 4998 | 7 | 6 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5743 | 4999 | 7 | 7 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5744 | 5000 | 7 | 8 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5745 | 5001 | 7 | 9 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5746 | 5002 | 7 | 10 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5747 | 5003 | 7 | 11 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5748 | 5004 | 7 | 12 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5749 | 5005 | 7 | 13 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5750 | 5006 | 7 | 14 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5751 | 5007 | 7 | 15 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5752 | 5008 | 7 | 16 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5753 | 5009 | 7 | 17 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5754 | 5010 | 7 | 18 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5755 | 5011 | 7 | 19 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5756 | 5012 | 7 | 20 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5757 | 5013 | 7 | 21 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5758 | 5014 | 7 | 22 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5759 | 5015 | 7 | 23 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5760 | 5016 | 7 | 24 | 209 | 43309 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5761 | 5017 | 7 | 1 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5762 | 5018 | 7 | 2 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5763 | 5019 | 7 | 3 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5764 | 5020 | 7 | 4 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5765 | 5021 | 7 | 5 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5766 | 5022 | 7 | 6 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5767 | 5023 | 7 | 7 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5768 | 5024 | 7 | 8 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5769 | 5025 | 7 | 9 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5770 | 5026 | 7 | 10 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5771 | 5027 | 7 | 11 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5772 | 5028 | 7 | 12 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5773 | 5029 | 7 | 13 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5774 | 5030 | 7 | 14 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5775 | 5031 | 7 | 15 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5776 | 5032 | 7 | 16 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5777 | 5033 | 7 | 17 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5778 | 5034 | 7 | 18 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5779 | 5035 | 7 | 19 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5780 | 5036 | 7 | 20 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5781 | 5037 | 7 | 21 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5782 | 5038 | 7 | 22 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5783 | 5039 | 7 | 23 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5784 | 5040 | 7 | 24 | 210 | 43310 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5785 | 5041 | 7 | 1 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5786 | 5042 | 7 | 2 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5787 | 5043 | 7 | 3 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5788 | 5044 | 7 | 4 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5789 | 5045 | 7 | 5 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5790 | 5046 | 7 | 6 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5791 | 5047 | 7 | 7 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5792 | 5048 | 7 | 8 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5793 | 5049 | 7 | 9 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5794 | 5050 | 7 | 10 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5795 | 5051 | 7 | 11 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5796 | 5052 | 7 | 12 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5797 | 5053 | 7 | 13 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5798 | 5054 | 7 | 14 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5799 | 5055 | 7 | 15 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5800 | 5056 | 7 | 16 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5801 | 5057 | 7 | 17 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5802 | 5058 | 7 | 18 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5803 | 5059 | 7 | 19 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5804 | 5060 | 7 | 20 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5805 | 5061 | 7 | 21 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5806 | 5062 | 7 | 22 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5807 | 5063 | 7 | 23 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5808 | 5064 | 7 | 24 | 211 | 43311 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5809 | 5065 | 7 | 1 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5810 | 5066 | 7 | 2 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5811 | 5067 | 7 | 3 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5812 | 5068 | 7 | 4 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5813 | 5069 | 7 | 5 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5814 | 5070 | 7 | 6 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5815 | 5071 | 7 | 7 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5816 | 5072 | 7 | 8 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5817 | 5073 | 7 | 9 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5818 | 5074 | 7 | 10 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5819 | 5075 | 7 | 11 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5820 | 5076 | 7 | 12 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5821 | 5077 | 7 | 13 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5822 | 5078 | 7 | 14 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5823 | 5079 | 7 | 15 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5824 | 5080 | 7 | 16 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5825 | 5081 | 7 | 17 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5826 | 5082 | 7 | 18 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5827 | 5083 | 7 | 19 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5828 | 5084 | 7 | 20 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5829 | 5085 | 7 | 21 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5830 | 5086 | 7 | 22 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5831 | 5087 | 7 | 23 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5832 | 5088 | 7 | 24 | 212 | 43312 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5833 | 5089 | 8 | 1 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5834 | 5090 | 8 | 2 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5835 | 5091 | 8 | 3 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5836 | 5092 | 8 | 4 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5837 | 5093 | 8 | 5 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5838 | 5094 | 8 | 6 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5839 | 5095 | 8 | 7 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5840 | 5096 | 8 | 8 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5841 | 5097 | 8 | 9 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5842 | 5098 | 8 | 10 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5843 | 5099 | 8 | 11 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5844 | 5100 | 8 | 12 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5845 | 5101 | 8 | 13 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5846 | 5102 | 8 | 14 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5847 | 5103 | 8 | 15 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5848 | 5104 | 8 | 16 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5849 | 5105 | 8 | 17 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5850 | 5106 | 8 | 18 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5851 | 5107 | 8 | 19 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5852 | 5108 | 8 | 20 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5853 | 5109 | 8 | 21 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5854 | 5110 | 8 | 22 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5855 | 5111 | 8 | 23 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5856 | 5112 | 8 | 24 | 213 | 43313 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5857 | 5113 | 8 | 1 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5858 | 5114 | 8 | 2 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5859 | 5115 | 8 | 3 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5860 | 5116 | 8 | 4 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5861 | 5117 | 8 | 5 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5862 | 5118 | 8 | 6 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5863 | 5119 | 8 | 7 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5864 | 5120 | 8 | 8 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5865 | 5121 | 8 | 9 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5866 | 5122 | 8 | 10 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5867 | 5123 | 8 | 11 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5868 | 5124 | 8 | 12 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5869 | 5125 | 8 | 13 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5870 | 5126 | 8 | 14 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5871 | 5127 | 8 | 15 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5872 | 5128 | 8 | 16 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5873 | 5129 | 8 | 17 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5874 | 5130 | 8 | 18 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5875 | 5131 | 8 | 19 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5876 | 5132 | 8 | 20 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5877 | 5133 | 8 | 21 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5878 | 5134 | 8 | 22 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5879 | 5135 | 8 | 23 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5880 | 5136 | 8 | 24 | 214 | 43314 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5881 | 5137 | 8 | 1 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5882 | 5138 | 8 | 2 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5883 | 5139 | 8 | 3 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5884 | 5140 | 8 | 4 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5885 | 5141 | 8 | 5 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5886 | 5142 | 8 | 6 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5887 | 5143 | 8 | 7 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5888 | 5144 | 8 | 8 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5889 | 5145 | 8 | 9 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5890 | 5146 | 8 | 10 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5891 | 5147 | 8 | 11 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5892 | 5148 | 8 | 12 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5893 | 5149 | 8 | 13 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5894 | 5150 | 8 | 14 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5895 | 5151 | 8 | 15 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5896 | 5152 | 8 | 16 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5897 | 5153 | 8 | 17 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5898 | 5154 | 8 | 18 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5899 | 5155 | 8 | 19 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5900 | 5156 | 8 | 20 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5901 | 5157 | 8 | 21 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5902 | 5158 | 8 | 22 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5903 | 5159 | 8 | 23 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5904 | 5160 | 8 | 24 | 215 | 43315 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5905 | 5161 | 8 | 1 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5906 | 5162 | 8 | 2 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5907 | 5163 | 8 | 3 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5908 | 5164 | 8 | 4 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5909 | 5165 | 8 | 5 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5910 | 5166 | 8 | 6 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5911 | 5167 | 8 | 7 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5912 | 5168 | 8 | 8 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5913 | 5169 | 8 | 9 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5914 | 5170 | 8 | 10 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5915 | 5171 | 8 | 11 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5916 | 5172 | 8 | 12 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5917 | 5173 | 8 | 13 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5918 | 5174 | 8 | 14 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5919 | 5175 | 8 | 15 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5920 | 5176 | 8 | 16 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5921 | 5177 | 8 | 17 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5922 | 5178 | 8 | 18 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5923 | 5179 | 8 | 19 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5924 | 5180 | 8 | 20 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5925 | 5181 | 8 | 21 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5926 | 5182 | 8 | 22 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5927 | 5183 | 8 | 23 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5928 | 5184 | 8 | 24 | 216 | 43316 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5929 | 5185 | 8 | 1 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5930 | 5186 | 8 | 2 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5931 | 5187 | 8 | 3 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5932 | 5188 | 8 | 4 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5933 | 5189 | 8 | 5 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5934 | 5190 | 8 | 6 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5935 | 5191 | 8 | 7 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5936 | 5192 | 8 | 8 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5937 | 5193 | 8 | 9 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5938 | 5194 | 8 | 10 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5939 | 5195 | 8 | 11 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5940 | 5196 | 8 | 12 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5941 | 5197 | 8 | 13 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5942 | 5198 | 8 | 14 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5943 | 5199 | 8 | 15 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5944 | 5200 | 8 | 16 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5945 | 5201 | 8 | 17 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5946 | 5202 | 8 | 18 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5947 | 5203 | 8 | 19 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5948 | 5204 | 8 | 20 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5949 | 5205 | 8 | 21 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5950 | 5206 | 8 | 22 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5951 | 5207 | 8 | 23 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5952 | 5208 | 8 | 24 | 217 | 43317 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5953 | 5209 | 8 | 1 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5954 | 5210 | 8 | 2 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5955 | 5211 | 8 | 3 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5956 | 5212 | 8 | 4 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5957 | 5213 | 8 | 5 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5958 | 5214 | 8 | 6 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5959 | 5215 | 8 | 7 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5960 | 5216 | 8 | 8 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5961 | 5217 | 8 | 9 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5962 | 5218 | 8 | 10 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5963 | 5219 | 8 | 11 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5964 | 5220 | 8 | 12 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5965 | 5221 | 8 | 13 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5966 | 5222 | 8 | 14 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5967 | 5223 | 8 | 15 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5968 | 5224 | 8 | 16 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5969 | 5225 | 8 | 17 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5970 | 5226 | 8 | 18 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5971 | 5227 | 8 | 19 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5972 | 5228 | 8 | 20 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5973 | 5229 | 8 | 21 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5974 | 5230 | 8 | 22 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5975 | 5231 | 8 | 23 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5976 | 5232 | 8 | 24 | 218 | 43318 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5977 | 5233 | 8 | 1 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5978 | 5234 | 8 | 2 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5979 | 5235 | 8 | 3 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5980 | 5236 | 8 | 4 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5981 | 5237 | 8 | 5 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5982 | 5238 | 8 | 6 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5983 | 5239 | 8 | 7 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5984 | 5240 | 8 | 8 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5985 | 5241 | 8 | 9 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5986 | 5242 | 8 | 10 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5987 | 5243 | 8 | 11 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5988 | 5244 | 8 | 12 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5989 | 5245 | 8 | 13 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5990 | 5246 | 8 | 14 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5991 | 5247 | 8 | 15 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5992 | 5248 | 8 | 16 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5993 | 5249 | 8 | 17 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5994 | 5250 | 8 | 18 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5995 | 5251 | 8 | 19 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5996 | 5252 | 8 | 20 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5997 | 5253 | 8 | 21 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5998 | 5254 | 8 | 22 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 5999 | 5255 | 8 | 23 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6000 | 5256 | 8 | 24 | 219 | 43319 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6001 | 5257 | 8 | 1 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6002 | 5258 | 8 | 2 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6003 | 5259 | 8 | 3 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6004 | 5260 | 8 | 4 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6005 | 5261 | 8 | 5 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6006 | 5262 | 8 | 6 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6007 | 5263 | 8 | 7 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6008 | 5264 | 8 | 8 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6009 | 5265 | 8 | 9 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6010 | 5266 | 8 | 10 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6011 | 5267 | 8 | 11 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6012 | 5268 | 8 | 12 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6013 | 5269 | 8 | 13 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6014 | 5270 | 8 | 14 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6015 | 5271 | 8 | 15 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6016 | 5272 | 8 | 16 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6017 | 5273 | 8 | 17 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6018 | 5274 | 8 | 18 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6019 | 5275 | 8 | 19 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6020 | 5276 | 8 | 20 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6021 | 5277 | 8 | 21 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6022 | 5278 | 8 | 22 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6023 | 5279 | 8 | 23 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6024 | 5280 | 8 | 24 | 220 | 43320 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6025 | 5281 | 8 | 1 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6026 | 5282 | 8 | 2 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6027 | 5283 | 8 | 3 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6028 | 5284 | 8 | 4 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6029 | 5285 | 8 | 5 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6030 | 5286 | 8 | 6 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6031 | 5287 | 8 | 7 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6032 | 5288 | 8 | 8 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6033 | 5289 | 8 | 9 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6034 | 5290 | 8 | 10 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6035 | 5291 | 8 | 11 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6036 | 5292 | 8 | 12 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6037 | 5293 | 8 | 13 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6038 | 5294 | 8 | 14 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6039 | 5295 | 8 | 15 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6040 | 5296 | 8 | 16 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6041 | 5297 | 8 | 17 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6042 | 5298 | 8 | 18 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6043 | 5299 | 8 | 19 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6044 | 5300 | 8 | 20 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6045 | 5301 | 8 | 21 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6046 | 5302 | 8 | 22 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6047 | 5303 | 8 | 23 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6048 | 5304 | 8 | 24 | 221 | 43321 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6049 | 5305 | 8 | 1 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6050 | 5306 | 8 | 2 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6051 | 5307 | 8 | 3 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6052 | 5308 | 8 | 4 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6053 | 5309 | 8 | 5 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6054 | 5310 | 8 | 6 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6055 | 5311 | 8 | 7 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6056 | 5312 | 8 | 8 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6057 | 5313 | 8 | 9 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6058 | 5314 | 8 | 10 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6059 | 5315 | 8 | 11 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6060 | 5316 | 8 | 12 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6061 | 5317 | 8 | 13 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6062 | 5318 | 8 | 14 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6063 | 5319 | 8 | 15 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6064 | 5320 | 8 | 16 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6065 | 5321 | 8 | 17 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6066 | 5322 | 8 | 18 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6067 | 5323 | 8 | 19 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6068 | 5324 | 8 | 20 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6069 | 5325 | 8 | 21 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6070 | 5326 | 8 | 22 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6071 | 5327 | 8 | 23 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6072 | 5328 | 8 | 24 | 222 | 43322 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6073 | 5329 | 8 | 1 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6074 | 5330 | 8 | 2 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6075 | 5331 | 8 | 3 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6076 | 5332 | 8 | 4 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6077 | 5333 | 8 | 5 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6078 | 5334 | 8 | 6 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6079 | 5335 | 8 | 7 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6080 | 5336 | 8 | 8 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6081 | 5337 | 8 | 9 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6082 | 5338 | 8 | 10 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6083 | 5339 | 8 | 11 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6084 | 5340 | 8 | 12 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6085 | 5341 | 8 | 13 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6086 | 5342 | 8 | 14 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6087 | 5343 | 8 | 15 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6088 | 5344 | 8 | 16 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6089 | 5345 | 8 | 17 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6090 | 5346 | 8 | 18 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6091 | 5347 | 8 | 19 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6092 | 5348 | 8 | 20 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6093 | 5349 | 8 | 21 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6094 | 5350 | 8 | 22 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6095 | 5351 | 8 | 23 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6096 | 5352 | 8 | 24 | 223 | 43323 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6097 | 5353 | 8 | 1 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6098 | 5354 | 8 | 2 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6099 | 5355 | 8 | 3 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6100 | 5356 | 8 | 4 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6101 | 5357 | 8 | 5 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6102 | 5358 | 8 | 6 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6103 | 5359 | 8 | 7 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6104 | 5360 | 8 | 8 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6105 | 5361 | 8 | 9 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6106 | 5362 | 8 | 10 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6107 | 5363 | 8 | 11 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6108 | 5364 | 8 | 12 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6109 | 5365 | 8 | 13 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6110 | 5366 | 8 | 14 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6111 | 5367 | 8 | 15 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6112 | 5368 | 8 | 16 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6113 | 5369 | 8 | 17 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6114 | 5370 | 8 | 18 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6115 | 5371 | 8 | 19 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6116 | 5372 | 8 | 20 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6117 | 5373 | 8 | 21 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6118 | 5374 | 8 | 22 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6119 | 5375 | 8 | 23 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6120 | 5376 | 8 | 24 | 224 | 43324 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6121 | 5377 | 8 | 1 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6122 | 5378 | 8 | 2 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6123 | 5379 | 8 | 3 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6124 | 5380 | 8 | 4 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6125 | 5381 | 8 | 5 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6126 | 5382 | 8 | 6 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6127 | 5383 | 8 | 7 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6128 | 5384 | 8 | 8 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6129 | 5385 | 8 | 9 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6130 | 5386 | 8 | 10 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6131 | 5387 | 8 | 11 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6132 | 5388 | 8 | 12 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6133 | 5389 | 8 | 13 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6134 | 5390 | 8 | 14 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6135 | 5391 | 8 | 15 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6136 | 5392 | 8 | 16 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6137 | 5393 | 8 | 17 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6138 | 5394 | 8 | 18 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6139 | 5395 | 8 | 19 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6140 | 5396 | 8 | 20 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6141 | 5397 | 8 | 21 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6142 | 5398 | 8 | 22 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6143 | 5399 | 8 | 23 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6144 | 5400 | 8 | 24 | 225 | 43325 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6145 | 5401 | 8 | 1 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6146 | 5402 | 8 | 2 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6147 | 5403 | 8 | 3 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6148 | 5404 | 8 | 4 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6149 | 5405 | 8 | 5 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6150 | 5406 | 8 | 6 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6151 | 5407 | 8 | 7 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6152 | 5408 | 8 | 8 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6153 | 5409 | 8 | 9 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6154 | 5410 | 8 | 10 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6155 | 5411 | 8 | 11 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6156 | 5412 | 8 | 12 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6157 | 5413 | 8 | 13 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6158 | 5414 | 8 | 14 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6159 | 5415 | 8 | 15 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6160 | 5416 | 8 | 16 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6161 | 5417 | 8 | 17 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6162 | 5418 | 8 | 18 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6163 | 5419 | 8 | 19 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6164 | 5420 | 8 | 20 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6165 | 5421 | 8 | 21 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6166 | 5422 | 8 | 22 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6167 | 5423 | 8 | 23 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6168 | 5424 | 8 | 24 | 226 | 43326 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6169 | 5425 | 8 | 1 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6170 | 5426 | 8 | 2 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6171 | 5427 | 8 | 3 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6172 | 5428 | 8 | 4 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6173 | 5429 | 8 | 5 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6174 | 5430 | 8 | 6 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6175 | 5431 | 8 | 7 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6176 | 5432 | 8 | 8 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6177 | 5433 | 8 | 9 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6178 | 5434 | 8 | 10 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6179 | 5435 | 8 | 11 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6180 | 5436 | 8 | 12 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6181 | 5437 | 8 | 13 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6182 | 5438 | 8 | 14 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6183 | 5439 | 8 | 15 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6184 | 5440 | 8 | 16 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6185 | 5441 | 8 | 17 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6186 | 5442 | 8 | 18 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6187 | 5443 | 8 | 19 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6188 | 5444 | 8 | 20 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6189 | 5445 | 8 | 21 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6190 | 5446 | 8 | 22 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6191 | 5447 | 8 | 23 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6192 | 5448 | 8 | 24 | 227 | 43327 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6193 | 5449 | 8 | 1 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6194 | 5450 | 8 | 2 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6195 | 5451 | 8 | 3 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6196 | 5452 | 8 | 4 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6197 | 5453 | 8 | 5 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6198 | 5454 | 8 | 6 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6199 | 5455 | 8 | 7 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6200 | 5456 | 8 | 8 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6201 | 5457 | 8 | 9 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6202 | 5458 | 8 | 10 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6203 | 5459 | 8 | 11 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6204 | 5460 | 8 | 12 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6205 | 5461 | 8 | 13 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6206 | 5462 | 8 | 14 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6207 | 5463 | 8 | 15 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6208 | 5464 | 8 | 16 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6209 | 5465 | 8 | 17 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6210 | 5466 | 8 | 18 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6211 | 5467 | 8 | 19 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6212 | 5468 | 8 | 20 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6213 | 5469 | 8 | 21 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6214 | 5470 | 8 | 22 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6215 | 5471 | 8 | 23 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6216 | 5472 | 8 | 24 | 228 | 43328 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6217 | 5473 | 8 | 1 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6218 | 5474 | 8 | 2 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6219 | 5475 | 8 | 3 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6220 | 5476 | 8 | 4 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6221 | 5477 | 8 | 5 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6222 | 5478 | 8 | 6 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6223 | 5479 | 8 | 7 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6224 | 5480 | 8 | 8 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6225 | 5481 | 8 | 9 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6226 | 5482 | 8 | 10 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6227 | 5483 | 8 | 11 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6228 | 5484 | 8 | 12 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6229 | 5485 | 8 | 13 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6230 | 5486 | 8 | 14 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6231 | 5487 | 8 | 15 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6232 | 5488 | 8 | 16 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6233 | 5489 | 8 | 17 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6234 | 5490 | 8 | 18 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6235 | 5491 | 8 | 19 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6236 | 5492 | 8 | 20 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6237 | 5493 | 8 | 21 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6238 | 5494 | 8 | 22 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6239 | 5495 | 8 | 23 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6240 | 5496 | 8 | 24 | 229 | 43329 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6241 | 5497 | 8 | 1 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6242 | 5498 | 8 | 2 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6243 | 5499 | 8 | 3 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6244 | 5500 | 8 | 4 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6245 | 5501 | 8 | 5 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6246 | 5502 | 8 | 6 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6247 | 5503 | 8 | 7 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6248 | 5504 | 8 | 8 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6249 | 5505 | 8 | 9 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6250 | 5506 | 8 | 10 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6251 | 5507 | 8 | 11 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6252 | 5508 | 8 | 12 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6253 | 5509 | 8 | 13 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6254 | 5510 | 8 | 14 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6255 | 5511 | 8 | 15 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6256 | 5512 | 8 | 16 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6257 | 5513 | 8 | 17 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6258 | 5514 | 8 | 18 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6259 | 5515 | 8 | 19 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6260 | 5516 | 8 | 20 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6261 | 5517 | 8 | 21 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6262 | 5518 | 8 | 22 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6263 | 5519 | 8 | 23 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6264 | 5520 | 8 | 24 | 230 | 43330 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6265 | 5521 | 8 | 1 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6266 | 5522 | 8 | 2 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6267 | 5523 | 8 | 3 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6268 | 5524 | 8 | 4 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6269 | 5525 | 8 | 5 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6270 | 5526 | 8 | 6 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6271 | 5527 | 8 | 7 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6272 | 5528 | 8 | 8 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6273 | 5529 | 8 | 9 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6274 | 5530 | 8 | 10 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6275 | 5531 | 8 | 11 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6276 | 5532 | 8 | 12 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6277 | 5533 | 8 | 13 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6278 | 5534 | 8 | 14 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6279 | 5535 | 8 | 15 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6280 | 5536 | 8 | 16 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6281 | 5537 | 8 | 17 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6282 | 5538 | 8 | 18 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6283 | 5539 | 8 | 19 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6284 | 5540 | 8 | 20 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6285 | 5541 | 8 | 21 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6286 | 5542 | 8 | 22 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6287 | 5543 | 8 | 23 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6288 | 5544 | 8 | 24 | 231 | 43331 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6289 | 5545 | 8 | 1 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6290 | 5546 | 8 | 2 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6291 | 5547 | 8 | 3 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6292 | 5548 | 8 | 4 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6293 | 5549 | 8 | 5 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6294 | 5550 | 8 | 6 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6295 | 5551 | 8 | 7 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6296 | 5552 | 8 | 8 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6297 | 5553 | 8 | 9 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6298 | 5554 | 8 | 10 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6299 | 5555 | 8 | 11 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6300 | 5556 | 8 | 12 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6301 | 5557 | 8 | 13 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6302 | 5558 | 8 | 14 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6303 | 5559 | 8 | 15 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6304 | 5560 | 8 | 16 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6305 | 5561 | 8 | 17 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6306 | 5562 | 8 | 18 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6307 | 5563 | 8 | 19 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6308 | 5564 | 8 | 20 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6309 | 5565 | 8 | 21 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6310 | 5566 | 8 | 22 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6311 | 5567 | 8 | 23 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6312 | 5568 | 8 | 24 | 232 | 43332 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6313 | 5569 | 8 | 1 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6314 | 5570 | 8 | 2 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6315 | 5571 | 8 | 3 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6316 | 5572 | 8 | 4 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6317 | 5573 | 8 | 5 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6318 | 5574 | 8 | 6 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6319 | 5575 | 8 | 7 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6320 | 5576 | 8 | 8 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6321 | 5577 | 8 | 9 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6322 | 5578 | 8 | 10 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6323 | 5579 | 8 | 11 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6324 | 5580 | 8 | 12 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6325 | 5581 | 8 | 13 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6326 | 5582 | 8 | 14 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6327 | 5583 | 8 | 15 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6328 | 5584 | 8 | 16 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6329 | 5585 | 8 | 17 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6330 | 5586 | 8 | 18 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6331 | 5587 | 8 | 19 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6332 | 5588 | 8 | 20 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6333 | 5589 | 8 | 21 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6334 | 5590 | 8 | 22 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6335 | 5591 | 8 | 23 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6336 | 5592 | 8 | 24 | 233 | 43333 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6337 | 5593 | 8 | 1 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6338 | 5594 | 8 | 2 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6339 | 5595 | 8 | 3 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6340 | 5596 | 8 | 4 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6341 | 5597 | 8 | 5 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6342 | 5598 | 8 | 6 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6343 | 5599 | 8 | 7 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6344 | 5600 | 8 | 8 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6345 | 5601 | 8 | 9 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6346 | 5602 | 8 | 10 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6347 | 5603 | 8 | 11 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6348 | 5604 | 8 | 12 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6349 | 5605 | 8 | 13 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6350 | 5606 | 8 | 14 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6351 | 5607 | 8 | 15 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6352 | 5608 | 8 | 16 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6353 | 5609 | 8 | 17 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6354 | 5610 | 8 | 18 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6355 | 5611 | 8 | 19 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6356 | 5612 | 8 | 20 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6357 | 5613 | 8 | 21 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6358 | 5614 | 8 | 22 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6359 | 5615 | 8 | 23 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6360 | 5616 | 8 | 24 | 234 | 43334 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6361 | 5617 | 8 | 1 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6362 | 5618 | 8 | 2 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6363 | 5619 | 8 | 3 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6364 | 5620 | 8 | 4 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6365 | 5621 | 8 | 5 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6366 | 5622 | 8 | 6 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6367 | 5623 | 8 | 7 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6368 | 5624 | 8 | 8 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6369 | 5625 | 8 | 9 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6370 | 5626 | 8 | 10 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6371 | 5627 | 8 | 11 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6372 | 5628 | 8 | 12 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6373 | 5629 | 8 | 13 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6374 | 5630 | 8 | 14 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6375 | 5631 | 8 | 15 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6376 | 5632 | 8 | 16 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6377 | 5633 | 8 | 17 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6378 | 5634 | 8 | 18 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6379 | 5635 | 8 | 19 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6380 | 5636 | 8 | 20 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6381 | 5637 | 8 | 21 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6382 | 5638 | 8 | 22 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6383 | 5639 | 8 | 23 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6384 | 5640 | 8 | 24 | 235 | 43335 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6385 | 5641 | 8 | 1 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6386 | 5642 | 8 | 2 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6387 | 5643 | 8 | 3 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6388 | 5644 | 8 | 4 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6389 | 5645 | 8 | 5 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6390 | 5646 | 8 | 6 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6391 | 5647 | 8 | 7 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6392 | 5648 | 8 | 8 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6393 | 5649 | 8 | 9 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6394 | 5650 | 8 | 10 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6395 | 5651 | 8 | 11 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6396 | 5652 | 8 | 12 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6397 | 5653 | 8 | 13 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6398 | 5654 | 8 | 14 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6399 | 5655 | 8 | 15 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6400 | 5656 | 8 | 16 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6401 | 5657 | 8 | 17 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6402 | 5658 | 8 | 18 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6403 | 5659 | 8 | 19 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6404 | 5660 | 8 | 20 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6405 | 5661 | 8 | 21 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6406 | 5662 | 8 | 22 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6407 | 5663 | 8 | 23 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6408 | 5664 | 8 | 24 | 236 | 43336 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6409 | 5665 | 8 | 1 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6410 | 5666 | 8 | 2 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6411 | 5667 | 8 | 3 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6412 | 5668 | 8 | 4 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6413 | 5669 | 8 | 5 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6414 | 5670 | 8 | 6 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6415 | 5671 | 8 | 7 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6416 | 5672 | 8 | 8 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6417 | 5673 | 8 | 9 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6418 | 5674 | 8 | 10 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6419 | 5675 | 8 | 11 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6420 | 5676 | 8 | 12 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6421 | 5677 | 8 | 13 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6422 | 5678 | 8 | 14 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6423 | 5679 | 8 | 15 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6424 | 5680 | 8 | 16 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6425 | 5681 | 8 | 17 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6426 | 5682 | 8 | 18 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6427 | 5683 | 8 | 19 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6428 | 5684 | 8 | 20 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6429 | 5685 | 8 | 21 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6430 | 5686 | 8 | 22 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6431 | 5687 | 8 | 23 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6432 | 5688 | 8 | 24 | 237 | 43337 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6433 | 5689 | 8 | 1 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6434 | 5690 | 8 | 2 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6435 | 5691 | 8 | 3 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6436 | 5692 | 8 | 4 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6437 | 5693 | 8 | 5 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6438 | 5694 | 8 | 6 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6439 | 5695 | 8 | 7 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6440 | 5696 | 8 | 8 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6441 | 5697 | 8 | 9 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6442 | 5698 | 8 | 10 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6443 | 5699 | 8 | 11 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6444 | 5700 | 8 | 12 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6445 | 5701 | 8 | 13 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6446 | 5702 | 8 | 14 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6447 | 5703 | 8 | 15 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6448 | 5704 | 8 | 16 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6449 | 5705 | 8 | 17 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6450 | 5706 | 8 | 18 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6451 | 5707 | 8 | 19 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6452 | 5708 | 8 | 20 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6453 | 5709 | 8 | 21 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6454 | 5710 | 8 | 22 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6455 | 5711 | 8 | 23 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6456 | 5712 | 8 | 24 | 238 | 43338 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6457 | 5713 | 8 | 1 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6458 | 5714 | 8 | 2 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6459 | 5715 | 8 | 3 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6460 | 5716 | 8 | 4 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6461 | 5717 | 8 | 5 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6462 | 5718 | 8 | 6 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6463 | 5719 | 8 | 7 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6464 | 5720 | 8 | 8 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6465 | 5721 | 8 | 9 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6466 | 5722 | 8 | 10 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6467 | 5723 | 8 | 11 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6468 | 5724 | 8 | 12 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6469 | 5725 | 8 | 13 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6470 | 5726 | 8 | 14 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6471 | 5727 | 8 | 15 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6472 | 5728 | 8 | 16 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6473 | 5729 | 8 | 17 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6474 | 5730 | 8 | 18 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6475 | 5731 | 8 | 19 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6476 | 5732 | 8 | 20 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6477 | 5733 | 8 | 21 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6478 | 5734 | 8 | 22 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6479 | 5735 | 8 | 23 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6480 | 5736 | 8 | 24 | 239 | 43339 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6481 | 5737 | 8 | 1 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6482 | 5738 | 8 | 2 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6483 | 5739 | 8 | 3 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6484 | 5740 | 8 | 4 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6485 | 5741 | 8 | 5 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6486 | 5742 | 8 | 6 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6487 | 5743 | 8 | 7 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6488 | 5744 | 8 | 8 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6489 | 5745 | 8 | 9 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6490 | 5746 | 8 | 10 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6491 | 5747 | 8 | 11 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6492 | 5748 | 8 | 12 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6493 | 5749 | 8 | 13 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6494 | 5750 | 8 | 14 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6495 | 5751 | 8 | 15 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6496 | 5752 | 8 | 16 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6497 | 5753 | 8 | 17 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6498 | 5754 | 8 | 18 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6499 | 5755 | 8 | 19 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6500 | 5756 | 8 | 20 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6501 | 5757 | 8 | 21 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6502 | 5758 | 8 | 22 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6503 | 5759 | 8 | 23 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6504 | 5760 | 8 | 24 | 240 | 43340 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6505 | 5761 | 8 | 1 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6506 | 5762 | 8 | 2 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6507 | 5763 | 8 | 3 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6508 | 5764 | 8 | 4 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6509 | 5765 | 8 | 5 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6510 | 5766 | 8 | 6 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6511 | 5767 | 8 | 7 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6512 | 5768 | 8 | 8 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6513 | 5769 | 8 | 9 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6514 | 5770 | 8 | 10 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6515 | 5771 | 8 | 11 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6516 | 5772 | 8 | 12 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6517 | 5773 | 8 | 13 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6518 | 5774 | 8 | 14 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6519 | 5775 | 8 | 15 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6520 | 5776 | 8 | 16 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6521 | 5777 | 8 | 17 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6522 | 5778 | 8 | 18 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6523 | 5779 | 8 | 19 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6524 | 5780 | 8 | 20 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6525 | 5781 | 8 | 21 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6526 | 5782 | 8 | 22 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6527 | 5783 | 8 | 23 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6528 | 5784 | 8 | 24 | 241 | 43341 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6529 | 5785 | 8 | 1 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6530 | 5786 | 8 | 2 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6531 | 5787 | 8 | 3 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6532 | 5788 | 8 | 4 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6533 | 5789 | 8 | 5 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6534 | 5790 | 8 | 6 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6535 | 5791 | 8 | 7 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6536 | 5792 | 8 | 8 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6537 | 5793 | 8 | 9 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6538 | 5794 | 8 | 10 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6539 | 5795 | 8 | 11 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6540 | 5796 | 8 | 12 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6541 | 5797 | 8 | 13 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6542 | 5798 | 8 | 14 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6543 | 5799 | 8 | 15 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6544 | 5800 | 8 | 16 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6545 | 5801 | 8 | 17 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6546 | 5802 | 8 | 18 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6547 | 5803 | 8 | 19 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6548 | 5804 | 8 | 20 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6549 | 5805 | 8 | 21 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6550 | 5806 | 8 | 22 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6551 | 5807 | 8 | 23 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6552 | 5808 | 8 | 24 | 242 | 43342 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6553 | 5809 | 8 | 1 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6554 | 5810 | 8 | 2 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6555 | 5811 | 8 | 3 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6556 | 5812 | 8 | 4 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6557 | 5813 | 8 | 5 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6558 | 5814 | 8 | 6 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6559 | 5815 | 8 | 7 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6560 | 5816 | 8 | 8 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6561 | 5817 | 8 | 9 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6562 | 5818 | 8 | 10 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6563 | 5819 | 8 | 11 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6564 | 5820 | 8 | 12 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6565 | 5821 | 8 | 13 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6566 | 5822 | 8 | 14 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6567 | 5823 | 8 | 15 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6568 | 5824 | 8 | 16 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6569 | 5825 | 8 | 17 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6570 | 5826 | 8 | 18 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6571 | 5827 | 8 | 19 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6572 | 5828 | 8 | 20 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6573 | 5829 | 8 | 21 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6574 | 5830 | 8 | 22 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6575 | 5831 | 8 | 23 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6576 | 5832 | 8 | 24 | 243 | 43343 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6577 | 5833 | 9 | 1 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6578 | 5834 | 9 | 2 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6579 | 5835 | 9 | 3 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6580 | 5836 | 9 | 4 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6581 | 5837 | 9 | 5 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6582 | 5838 | 9 | 6 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6583 | 5839 | 9 | 7 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6584 | 5840 | 9 | 8 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6585 | 5841 | 9 | 9 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6586 | 5842 | 9 | 10 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6587 | 5843 | 9 | 11 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6588 | 5844 | 9 | 12 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6589 | 5845 | 9 | 13 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6590 | 5846 | 9 | 14 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6591 | 5847 | 9 | 15 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6592 | 5848 | 9 | 16 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6593 | 5849 | 9 | 17 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6594 | 5850 | 9 | 18 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6595 | 5851 | 9 | 19 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6596 | 5852 | 9 | 20 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6597 | 5853 | 9 | 21 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6598 | 5854 | 9 | 22 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6599 | 5855 | 9 | 23 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6600 | 5856 | 9 | 24 | 244 | 43344 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6601 | 5857 | 9 | 1 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6602 | 5858 | 9 | 2 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6603 | 5859 | 9 | 3 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6604 | 5860 | 9 | 4 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6605 | 5861 | 9 | 5 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6606 | 5862 | 9 | 6 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6607 | 5863 | 9 | 7 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6608 | 5864 | 9 | 8 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6609 | 5865 | 9 | 9 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6610 | 5866 | 9 | 10 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6611 | 5867 | 9 | 11 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6612 | 5868 | 9 | 12 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6613 | 5869 | 9 | 13 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6614 | 5870 | 9 | 14 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6615 | 5871 | 9 | 15 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6616 | 5872 | 9 | 16 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6617 | 5873 | 9 | 17 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6618 | 5874 | 9 | 18 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6619 | 5875 | 9 | 19 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6620 | 5876 | 9 | 20 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6621 | 5877 | 9 | 21 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6622 | 5878 | 9 | 22 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6623 | 5879 | 9 | 23 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6624 | 5880 | 9 | 24 | 245 | 43345 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6625 | 5881 | 9 | 1 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6626 | 5882 | 9 | 2 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6627 | 5883 | 9 | 3 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6628 | 5884 | 9 | 4 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6629 | 5885 | 9 | 5 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6630 | 5886 | 9 | 6 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6631 | 5887 | 9 | 7 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6632 | 5888 | 9 | 8 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6633 | 5889 | 9 | 9 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6634 | 5890 | 9 | 10 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6635 | 5891 | 9 | 11 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6636 | 5892 | 9 | 12 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6637 | 5893 | 9 | 13 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6638 | 5894 | 9 | 14 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6639 | 5895 | 9 | 15 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6640 | 5896 | 9 | 16 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6641 | 5897 | 9 | 17 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6642 | 5898 | 9 | 18 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6643 | 5899 | 9 | 19 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6644 | 5900 | 9 | 20 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6645 | 5901 | 9 | 21 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6646 | 5902 | 9 | 22 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6647 | 5903 | 9 | 23 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6648 | 5904 | 9 | 24 | 246 | 43346 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6649 | 5905 | 9 | 1 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6650 | 5906 | 9 | 2 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6651 | 5907 | 9 | 3 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6652 | 5908 | 9 | 4 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6653 | 5909 | 9 | 5 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6654 | 5910 | 9 | 6 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6655 | 5911 | 9 | 7 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6656 | 5912 | 9 | 8 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6657 | 5913 | 9 | 9 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6658 | 5914 | 9 | 10 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6659 | 5915 | 9 | 11 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6660 | 5916 | 9 | 12 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6661 | 5917 | 9 | 13 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6662 | 5918 | 9 | 14 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6663 | 5919 | 9 | 15 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6664 | 5920 | 9 | 16 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6665 | 5921 | 9 | 17 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6666 | 5922 | 9 | 18 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6667 | 5923 | 9 | 19 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6668 | 5924 | 9 | 20 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6669 | 5925 | 9 | 21 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6670 | 5926 | 9 | 22 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6671 | 5927 | 9 | 23 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6672 | 5928 | 9 | 24 | 247 | 43347 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6673 | 5929 | 9 | 1 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6674 | 5930 | 9 | 2 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6675 | 5931 | 9 | 3 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6676 | 5932 | 9 | 4 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6677 | 5933 | 9 | 5 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6678 | 5934 | 9 | 6 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6679 | 5935 | 9 | 7 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6680 | 5936 | 9 | 8 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6681 | 5937 | 9 | 9 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6682 | 5938 | 9 | 10 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6683 | 5939 | 9 | 11 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6684 | 5940 | 9 | 12 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6685 | 5941 | 9 | 13 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6686 | 5942 | 9 | 14 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6687 | 5943 | 9 | 15 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6688 | 5944 | 9 | 16 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6689 | 5945 | 9 | 17 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6690 | 5946 | 9 | 18 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6691 | 5947 | 9 | 19 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6692 | 5948 | 9 | 20 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6693 | 5949 | 9 | 21 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6694 | 5950 | 9 | 22 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6695 | 5951 | 9 | 23 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6696 | 5952 | 9 | 24 | 248 | 43348 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6697 | 5953 | 9 | 1 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6698 | 5954 | 9 | 2 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6699 | 5955 | 9 | 3 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6700 | 5956 | 9 | 4 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6701 | 5957 | 9 | 5 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6702 | 5958 | 9 | 6 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6703 | 5959 | 9 | 7 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6704 | 5960 | 9 | 8 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6705 | 5961 | 9 | 9 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6706 | 5962 | 9 | 10 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6707 | 5963 | 9 | 11 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6708 | 5964 | 9 | 12 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6709 | 5965 | 9 | 13 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6710 | 5966 | 9 | 14 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6711 | 5967 | 9 | 15 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6712 | 5968 | 9 | 16 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6713 | 5969 | 9 | 17 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6714 | 5970 | 9 | 18 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6715 | 5971 | 9 | 19 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6716 | 5972 | 9 | 20 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6717 | 5973 | 9 | 21 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6718 | 5974 | 9 | 22 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6719 | 5975 | 9 | 23 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6720 | 5976 | 9 | 24 | 249 | 43349 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6721 | 5977 | 9 | 1 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6722 | 5978 | 9 | 2 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6723 | 5979 | 9 | 3 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6724 | 5980 | 9 | 4 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6725 | 5981 | 9 | 5 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6726 | 5982 | 9 | 6 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6727 | 5983 | 9 | 7 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6728 | 5984 | 9 | 8 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6729 | 5985 | 9 | 9 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6730 | 5986 | 9 | 10 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6731 | 5987 | 9 | 11 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6732 | 5988 | 9 | 12 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6733 | 5989 | 9 | 13 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6734 | 5990 | 9 | 14 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6735 | 5991 | 9 | 15 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6736 | 5992 | 9 | 16 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6737 | 5993 | 9 | 17 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6738 | 5994 | 9 | 18 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6739 | 5995 | 9 | 19 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6740 | 5996 | 9 | 20 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6741 | 5997 | 9 | 21 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6742 | 5998 | 9 | 22 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6743 | 5999 | 9 | 23 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6744 | 6000 | 9 | 24 | 250 | 43350 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6745 | 6001 | 9 | 1 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6746 | 6002 | 9 | 2 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6747 | 6003 | 9 | 3 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6748 | 6004 | 9 | 4 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6749 | 6005 | 9 | 5 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6750 | 6006 | 9 | 6 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6751 | 6007 | 9 | 7 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6752 | 6008 | 9 | 8 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6753 | 6009 | 9 | 9 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6754 | 6010 | 9 | 10 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6755 | 6011 | 9 | 11 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6756 | 6012 | 9 | 12 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6757 | 6013 | 9 | 13 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6758 | 6014 | 9 | 14 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6759 | 6015 | 9 | 15 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6760 | 6016 | 9 | 16 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6761 | 6017 | 9 | 17 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6762 | 6018 | 9 | 18 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6763 | 6019 | 9 | 19 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6764 | 6020 | 9 | 20 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6765 | 6021 | 9 | 21 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6766 | 6022 | 9 | 22 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6767 | 6023 | 9 | 23 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6768 | 6024 | 9 | 24 | 251 | 43351 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6769 | 6025 | 9 | 1 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6770 | 6026 | 9 | 2 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6771 | 6027 | 9 | 3 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6772 | 6028 | 9 | 4 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6773 | 6029 | 9 | 5 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6774 | 6030 | 9 | 6 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6775 | 6031 | 9 | 7 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6776 | 6032 | 9 | 8 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6777 | 6033 | 9 | 9 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6778 | 6034 | 9 | 10 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6779 | 6035 | 9 | 11 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6780 | 6036 | 9 | 12 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6781 | 6037 | 9 | 13 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6782 | 6038 | 9 | 14 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6783 | 6039 | 9 | 15 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6784 | 6040 | 9 | 16 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6785 | 6041 | 9 | 17 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6786 | 6042 | 9 | 18 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6787 | 6043 | 9 | 19 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6788 | 6044 | 9 | 20 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6789 | 6045 | 9 | 21 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6790 | 6046 | 9 | 22 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6791 | 6047 | 9 | 23 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6792 | 6048 | 9 | 24 | 252 | 43352 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6793 | 6049 | 9 | 1 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6794 | 6050 | 9 | 2 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6795 | 6051 | 9 | 3 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6796 | 6052 | 9 | 4 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6797 | 6053 | 9 | 5 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6798 | 6054 | 9 | 6 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6799 | 6055 | 9 | 7 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6800 | 6056 | 9 | 8 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6801 | 6057 | 9 | 9 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6802 | 6058 | 9 | 10 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6803 | 6059 | 9 | 11 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6804 | 6060 | 9 | 12 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6805 | 6061 | 9 | 13 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6806 | 6062 | 9 | 14 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6807 | 6063 | 9 | 15 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6808 | 6064 | 9 | 16 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6809 | 6065 | 9 | 17 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6810 | 6066 | 9 | 18 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6811 | 6067 | 9 | 19 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6812 | 6068 | 9 | 20 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6813 | 6069 | 9 | 21 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6814 | 6070 | 9 | 22 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6815 | 6071 | 9 | 23 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6816 | 6072 | 9 | 24 | 253 | 43353 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6817 | 6073 | 9 | 1 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6818 | 6074 | 9 | 2 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6819 | 6075 | 9 | 3 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6820 | 6076 | 9 | 4 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6821 | 6077 | 9 | 5 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6822 | 6078 | 9 | 6 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6823 | 6079 | 9 | 7 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6824 | 6080 | 9 | 8 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6825 | 6081 | 9 | 9 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6826 | 6082 | 9 | 10 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6827 | 6083 | 9 | 11 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6828 | 6084 | 9 | 12 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6829 | 6085 | 9 | 13 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6830 | 6086 | 9 | 14 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6831 | 6087 | 9 | 15 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6832 | 6088 | 9 | 16 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6833 | 6089 | 9 | 17 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6834 | 6090 | 9 | 18 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6835 | 6091 | 9 | 19 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6836 | 6092 | 9 | 20 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6837 | 6093 | 9 | 21 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6838 | 6094 | 9 | 22 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6839 | 6095 | 9 | 23 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6840 | 6096 | 9 | 24 | 254 | 43354 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6841 | 6097 | 9 | 1 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6842 | 6098 | 9 | 2 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6843 | 6099 | 9 | 3 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6844 | 6100 | 9 | 4 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6845 | 6101 | 9 | 5 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6846 | 6102 | 9 | 6 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6847 | 6103 | 9 | 7 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6848 | 6104 | 9 | 8 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6849 | 6105 | 9 | 9 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6850 | 6106 | 9 | 10 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6851 | 6107 | 9 | 11 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6852 | 6108 | 9 | 12 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6853 | 6109 | 9 | 13 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6854 | 6110 | 9 | 14 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6855 | 6111 | 9 | 15 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6856 | 6112 | 9 | 16 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6857 | 6113 | 9 | 17 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6858 | 6114 | 9 | 18 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6859 | 6115 | 9 | 19 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6860 | 6116 | 9 | 20 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6861 | 6117 | 9 | 21 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6862 | 6118 | 9 | 22 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6863 | 6119 | 9 | 23 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6864 | 6120 | 9 | 24 | 255 | 43355 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6865 | 6121 | 9 | 1 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6866 | 6122 | 9 | 2 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6867 | 6123 | 9 | 3 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6868 | 6124 | 9 | 4 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6869 | 6125 | 9 | 5 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6870 | 6126 | 9 | 6 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6871 | 6127 | 9 | 7 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6872 | 6128 | 9 | 8 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6873 | 6129 | 9 | 9 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6874 | 6130 | 9 | 10 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6875 | 6131 | 9 | 11 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6876 | 6132 | 9 | 12 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6877 | 6133 | 9 | 13 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6878 | 6134 | 9 | 14 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6879 | 6135 | 9 | 15 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6880 | 6136 | 9 | 16 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6881 | 6137 | 9 | 17 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6882 | 6138 | 9 | 18 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6883 | 6139 | 9 | 19 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6884 | 6140 | 9 | 20 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6885 | 6141 | 9 | 21 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6886 | 6142 | 9 | 22 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6887 | 6143 | 9 | 23 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6888 | 6144 | 9 | 24 | 256 | 43356 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6889 | 6145 | 9 | 1 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6890 | 6146 | 9 | 2 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6891 | 6147 | 9 | 3 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6892 | 6148 | 9 | 4 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6893 | 6149 | 9 | 5 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6894 | 6150 | 9 | 6 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6895 | 6151 | 9 | 7 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6896 | 6152 | 9 | 8 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6897 | 6153 | 9 | 9 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6898 | 6154 | 9 | 10 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6899 | 6155 | 9 | 11 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6900 | 6156 | 9 | 12 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6901 | 6157 | 9 | 13 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6902 | 6158 | 9 | 14 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6903 | 6159 | 9 | 15 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6904 | 6160 | 9 | 16 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6905 | 6161 | 9 | 17 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6906 | 6162 | 9 | 18 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6907 | 6163 | 9 | 19 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6908 | 6164 | 9 | 20 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6909 | 6165 | 9 | 21 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6910 | 6166 | 9 | 22 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6911 | 6167 | 9 | 23 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6912 | 6168 | 9 | 24 | 257 | 43357 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6913 | 6169 | 9 | 1 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6914 | 6170 | 9 | 2 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6915 | 6171 | 9 | 3 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6916 | 6172 | 9 | 4 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6917 | 6173 | 9 | 5 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6918 | 6174 | 9 | 6 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6919 | 6175 | 9 | 7 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6920 | 6176 | 9 | 8 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6921 | 6177 | 9 | 9 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6922 | 6178 | 9 | 10 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6923 | 6179 | 9 | 11 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6924 | 6180 | 9 | 12 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6925 | 6181 | 9 | 13 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6926 | 6182 | 9 | 14 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6927 | 6183 | 9 | 15 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6928 | 6184 | 9 | 16 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6929 | 6185 | 9 | 17 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6930 | 6186 | 9 | 18 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6931 | 6187 | 9 | 19 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6932 | 6188 | 9 | 20 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6933 | 6189 | 9 | 21 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6934 | 6190 | 9 | 22 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6935 | 6191 | 9 | 23 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6936 | 6192 | 9 | 24 | 258 | 43358 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6937 | 6193 | 9 | 1 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6938 | 6194 | 9 | 2 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6939 | 6195 | 9 | 3 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6940 | 6196 | 9 | 4 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6941 | 6197 | 9 | 5 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6942 | 6198 | 9 | 6 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6943 | 6199 | 9 | 7 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6944 | 6200 | 9 | 8 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6945 | 6201 | 9 | 9 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6946 | 6202 | 9 | 10 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6947 | 6203 | 9 | 11 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6948 | 6204 | 9 | 12 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6949 | 6205 | 9 | 13 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6950 | 6206 | 9 | 14 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6951 | 6207 | 9 | 15 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6952 | 6208 | 9 | 16 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6953 | 6209 | 9 | 17 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6954 | 6210 | 9 | 18 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6955 | 6211 | 9 | 19 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6956 | 6212 | 9 | 20 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6957 | 6213 | 9 | 21 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6958 | 6214 | 9 | 22 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6959 | 6215 | 9 | 23 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6960 | 6216 | 9 | 24 | 259 | 43359 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6961 | 6217 | 9 | 1 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6962 | 6218 | 9 | 2 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6963 | 6219 | 9 | 3 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6964 | 6220 | 9 | 4 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6965 | 6221 | 9 | 5 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6966 | 6222 | 9 | 6 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6967 | 6223 | 9 | 7 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6968 | 6224 | 9 | 8 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6969 | 6225 | 9 | 9 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6970 | 6226 | 9 | 10 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6971 | 6227 | 9 | 11 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6972 | 6228 | 9 | 12 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6973 | 6229 | 9 | 13 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6974 | 6230 | 9 | 14 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6975 | 6231 | 9 | 15 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6976 | 6232 | 9 | 16 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6977 | 6233 | 9 | 17 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6978 | 6234 | 9 | 18 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6979 | 6235 | 9 | 19 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6980 | 6236 | 9 | 20 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6981 | 6237 | 9 | 21 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6982 | 6238 | 9 | 22 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6983 | 6239 | 9 | 23 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6984 | 6240 | 9 | 24 | 260 | 43360 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6985 | 6241 | 9 | 1 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6986 | 6242 | 9 | 2 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6987 | 6243 | 9 | 3 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6988 | 6244 | 9 | 4 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6989 | 6245 | 9 | 5 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6990 | 6246 | 9 | 6 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6991 | 6247 | 9 | 7 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6992 | 6248 | 9 | 8 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6993 | 6249 | 9 | 9 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6994 | 6250 | 9 | 10 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6995 | 6251 | 9 | 11 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6996 | 6252 | 9 | 12 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6997 | 6253 | 9 | 13 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6998 | 6254 | 9 | 14 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 6999 | 6255 | 9 | 15 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7000 | 6256 | 9 | 16 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7001 | 6257 | 9 | 17 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7002 | 6258 | 9 | 18 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7003 | 6259 | 9 | 19 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7004 | 6260 | 9 | 20 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7005 | 6261 | 9 | 21 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7006 | 6262 | 9 | 22 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7007 | 6263 | 9 | 23 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7008 | 6264 | 9 | 24 | 261 | 43361 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7009 | 6265 | 9 | 1 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7010 | 6266 | 9 | 2 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7011 | 6267 | 9 | 3 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7012 | 6268 | 9 | 4 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7013 | 6269 | 9 | 5 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7014 | 6270 | 9 | 6 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7015 | 6271 | 9 | 7 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7016 | 6272 | 9 | 8 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7017 | 6273 | 9 | 9 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7018 | 6274 | 9 | 10 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7019 | 6275 | 9 | 11 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7020 | 6276 | 9 | 12 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7021 | 6277 | 9 | 13 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7022 | 6278 | 9 | 14 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7023 | 6279 | 9 | 15 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7024 | 6280 | 9 | 16 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7025 | 6281 | 9 | 17 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7026 | 6282 | 9 | 18 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7027 | 6283 | 9 | 19 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7028 | 6284 | 9 | 20 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7029 | 6285 | 9 | 21 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7030 | 6286 | 9 | 22 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7031 | 6287 | 9 | 23 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7032 | 6288 | 9 | 24 | 262 | 43362 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7033 | 6289 | 9 | 1 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7034 | 6290 | 9 | 2 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7035 | 6291 | 9 | 3 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7036 | 6292 | 9 | 4 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7037 | 6293 | 9 | 5 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7038 | 6294 | 9 | 6 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7039 | 6295 | 9 | 7 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7040 | 6296 | 9 | 8 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7041 | 6297 | 9 | 9 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7042 | 6298 | 9 | 10 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7043 | 6299 | 9 | 11 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7044 | 6300 | 9 | 12 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7045 | 6301 | 9 | 13 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7046 | 6302 | 9 | 14 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7047 | 6303 | 9 | 15 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7048 | 6304 | 9 | 16 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7049 | 6305 | 9 | 17 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7050 | 6306 | 9 | 18 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7051 | 6307 | 9 | 19 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7052 | 6308 | 9 | 20 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7053 | 6309 | 9 | 21 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7054 | 6310 | 9 | 22 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7055 | 6311 | 9 | 23 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7056 | 6312 | 9 | 24 | 263 | 43363 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7057 | 6313 | 9 | 1 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7058 | 6314 | 9 | 2 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7059 | 6315 | 9 | 3 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7060 | 6316 | 9 | 4 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7061 | 6317 | 9 | 5 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7062 | 6318 | 9 | 6 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7063 | 6319 | 9 | 7 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7064 | 6320 | 9 | 8 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7065 | 6321 | 9 | 9 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7066 | 6322 | 9 | 10 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7067 | 6323 | 9 | 11 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7068 | 6324 | 9 | 12 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7069 | 6325 | 9 | 13 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7070 | 6326 | 9 | 14 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7071 | 6327 | 9 | 15 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7072 | 6328 | 9 | 16 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7073 | 6329 | 9 | 17 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7074 | 6330 | 9 | 18 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7075 | 6331 | 9 | 19 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7076 | 6332 | 9 | 20 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7077 | 6333 | 9 | 21 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7078 | 6334 | 9 | 22 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7079 | 6335 | 9 | 23 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7080 | 6336 | 9 | 24 | 264 | 43364 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7081 | 6337 | 9 | 1 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7082 | 6338 | 9 | 2 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7083 | 6339 | 9 | 3 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7084 | 6340 | 9 | 4 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7085 | 6341 | 9 | 5 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7086 | 6342 | 9 | 6 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7087 | 6343 | 9 | 7 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7088 | 6344 | 9 | 8 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7089 | 6345 | 9 | 9 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7090 | 6346 | 9 | 10 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7091 | 6347 | 9 | 11 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7092 | 6348 | 9 | 12 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7093 | 6349 | 9 | 13 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7094 | 6350 | 9 | 14 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7095 | 6351 | 9 | 15 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7096 | 6352 | 9 | 16 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7097 | 6353 | 9 | 17 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7098 | 6354 | 9 | 18 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7099 | 6355 | 9 | 19 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7100 | 6356 | 9 | 20 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7101 | 6357 | 9 | 21 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7102 | 6358 | 9 | 22 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7103 | 6359 | 9 | 23 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7104 | 6360 | 9 | 24 | 265 | 43365 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7105 | 6361 | 9 | 1 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7106 | 6362 | 9 | 2 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7107 | 6363 | 9 | 3 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7108 | 6364 | 9 | 4 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7109 | 6365 | 9 | 5 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7110 | 6366 | 9 | 6 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7111 | 6367 | 9 | 7 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7112 | 6368 | 9 | 8 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7113 | 6369 | 9 | 9 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7114 | 6370 | 9 | 10 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7115 | 6371 | 9 | 11 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7116 | 6372 | 9 | 12 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7117 | 6373 | 9 | 13 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7118 | 6374 | 9 | 14 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7119 | 6375 | 9 | 15 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7120 | 6376 | 9 | 16 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7121 | 6377 | 9 | 17 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7122 | 6378 | 9 | 18 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7123 | 6379 | 9 | 19 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7124 | 6380 | 9 | 20 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7125 | 6381 | 9 | 21 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7126 | 6382 | 9 | 22 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7127 | 6383 | 9 | 23 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7128 | 6384 | 9 | 24 | 266 | 43366 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7129 | 6385 | 9 | 1 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7130 | 6386 | 9 | 2 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7131 | 6387 | 9 | 3 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7132 | 6388 | 9 | 4 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7133 | 6389 | 9 | 5 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7134 | 6390 | 9 | 6 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7135 | 6391 | 9 | 7 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7136 | 6392 | 9 | 8 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7137 | 6393 | 9 | 9 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7138 | 6394 | 9 | 10 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7139 | 6395 | 9 | 11 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7140 | 6396 | 9 | 12 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7141 | 6397 | 9 | 13 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7142 | 6398 | 9 | 14 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7143 | 6399 | 9 | 15 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7144 | 6400 | 9 | 16 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7145 | 6401 | 9 | 17 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7146 | 6402 | 9 | 18 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7147 | 6403 | 9 | 19 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7148 | 6404 | 9 | 20 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7149 | 6405 | 9 | 21 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7150 | 6406 | 9 | 22 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7151 | 6407 | 9 | 23 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7152 | 6408 | 9 | 24 | 267 | 43367 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7153 | 6409 | 9 | 1 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7154 | 6410 | 9 | 2 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7155 | 6411 | 9 | 3 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7156 | 6412 | 9 | 4 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7157 | 6413 | 9 | 5 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7158 | 6414 | 9 | 6 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7159 | 6415 | 9 | 7 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7160 | 6416 | 9 | 8 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7161 | 6417 | 9 | 9 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7162 | 6418 | 9 | 10 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7163 | 6419 | 9 | 11 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7164 | 6420 | 9 | 12 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7165 | 6421 | 9 | 13 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7166 | 6422 | 9 | 14 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7167 | 6423 | 9 | 15 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7168 | 6424 | 9 | 16 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7169 | 6425 | 9 | 17 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7170 | 6426 | 9 | 18 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7171 | 6427 | 9 | 19 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7172 | 6428 | 9 | 20 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7173 | 6429 | 9 | 21 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7174 | 6430 | 9 | 22 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7175 | 6431 | 9 | 23 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7176 | 6432 | 9 | 24 | 268 | 43368 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7177 | 6433 | 9 | 1 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7178 | 6434 | 9 | 2 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7179 | 6435 | 9 | 3 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7180 | 6436 | 9 | 4 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7181 | 6437 | 9 | 5 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7182 | 6438 | 9 | 6 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7183 | 6439 | 9 | 7 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7184 | 6440 | 9 | 8 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7185 | 6441 | 9 | 9 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7186 | 6442 | 9 | 10 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7187 | 6443 | 9 | 11 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7188 | 6444 | 9 | 12 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7189 | 6445 | 9 | 13 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7190 | 6446 | 9 | 14 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7191 | 6447 | 9 | 15 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7192 | 6448 | 9 | 16 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7193 | 6449 | 9 | 17 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7194 | 6450 | 9 | 18 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7195 | 6451 | 9 | 19 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7196 | 6452 | 9 | 20 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7197 | 6453 | 9 | 21 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7198 | 6454 | 9 | 22 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7199 | 6455 | 9 | 23 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7200 | 6456 | 9 | 24 | 269 | 43369 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7201 | 6457 | 9 | 1 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7202 | 6458 | 9 | 2 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7203 | 6459 | 9 | 3 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7204 | 6460 | 9 | 4 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7205 | 6461 | 9 | 5 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7206 | 6462 | 9 | 6 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7207 | 6463 | 9 | 7 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7208 | 6464 | 9 | 8 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7209 | 6465 | 9 | 9 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7210 | 6466 | 9 | 10 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7211 | 6467 | 9 | 11 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7212 | 6468 | 9 | 12 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7213 | 6469 | 9 | 13 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7214 | 6470 | 9 | 14 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7215 | 6471 | 9 | 15 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7216 | 6472 | 9 | 16 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7217 | 6473 | 9 | 17 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7218 | 6474 | 9 | 18 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7219 | 6475 | 9 | 19 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7220 | 6476 | 9 | 20 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7221 | 6477 | 9 | 21 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7222 | 6478 | 9 | 22 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7223 | 6479 | 9 | 23 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7224 | 6480 | 9 | 24 | 270 | 43370 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7225 | 6481 | 9 | 1 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7226 | 6482 | 9 | 2 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7227 | 6483 | 9 | 3 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7228 | 6484 | 9 | 4 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7229 | 6485 | 9 | 5 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7230 | 6486 | 9 | 6 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7231 | 6487 | 9 | 7 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7232 | 6488 | 9 | 8 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7233 | 6489 | 9 | 9 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7234 | 6490 | 9 | 10 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7235 | 6491 | 9 | 11 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7236 | 6492 | 9 | 12 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7237 | 6493 | 9 | 13 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7238 | 6494 | 9 | 14 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7239 | 6495 | 9 | 15 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7240 | 6496 | 9 | 16 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7241 | 6497 | 9 | 17 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7242 | 6498 | 9 | 18 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7243 | 6499 | 9 | 19 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7244 | 6500 | 9 | 20 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7245 | 6501 | 9 | 21 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7246 | 6502 | 9 | 22 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7247 | 6503 | 9 | 23 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7248 | 6504 | 9 | 24 | 271 | 43371 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7249 | 6505 | 9 | 1 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7250 | 6506 | 9 | 2 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7251 | 6507 | 9 | 3 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7252 | 6508 | 9 | 4 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7253 | 6509 | 9 | 5 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7254 | 6510 | 9 | 6 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7255 | 6511 | 9 | 7 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7256 | 6512 | 9 | 8 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7257 | 6513 | 9 | 9 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7258 | 6514 | 9 | 10 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7259 | 6515 | 9 | 11 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7260 | 6516 | 9 | 12 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7261 | 6517 | 9 | 13 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7262 | 6518 | 9 | 14 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7263 | 6519 | 9 | 15 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7264 | 6520 | 9 | 16 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7265 | 6521 | 9 | 17 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7266 | 6522 | 9 | 18 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7267 | 6523 | 9 | 19 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7268 | 6524 | 9 | 20 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7269 | 6525 | 9 | 21 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7270 | 6526 | 9 | 22 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7271 | 6527 | 9 | 23 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7272 | 6528 | 9 | 24 | 272 | 43372 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7273 | 6529 | 9 | 1 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7274 | 6530 | 9 | 2 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7275 | 6531 | 9 | 3 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7276 | 6532 | 9 | 4 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7277 | 6533 | 9 | 5 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7278 | 6534 | 9 | 6 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7279 | 6535 | 9 | 7 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7280 | 6536 | 9 | 8 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7281 | 6537 | 9 | 9 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7282 | 6538 | 9 | 10 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7283 | 6539 | 9 | 11 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7284 | 6540 | 9 | 12 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7285 | 6541 | 9 | 13 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7286 | 6542 | 9 | 14 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7287 | 6543 | 9 | 15 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7288 | 6544 | 9 | 16 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7289 | 6545 | 9 | 17 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7290 | 6546 | 9 | 18 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7291 | 6547 | 9 | 19 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7292 | 6548 | 9 | 20 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7293 | 6549 | 9 | 21 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7294 | 6550 | 9 | 22 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7295 | 6551 | 9 | 23 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7296 | 6552 | 9 | 24 | 273 | 43373 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7297 | 6553 | 10 | 1 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7298 | 6554 | 10 | 2 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7299 | 6555 | 10 | 3 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7300 | 6556 | 10 | 4 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7301 | 6557 | 10 | 5 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7302 | 6558 | 10 | 6 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7303 | 6559 | 10 | 7 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7304 | 6560 | 10 | 8 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7305 | 6561 | 10 | 9 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7306 | 6562 | 10 | 10 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7307 | 6563 | 10 | 11 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7308 | 6564 | 10 | 12 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7309 | 6565 | 10 | 13 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7310 | 6566 | 10 | 14 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7311 | 6567 | 10 | 15 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7312 | 6568 | 10 | 16 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7313 | 6569 | 10 | 17 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7314 | 6570 | 10 | 18 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7315 | 6571 | 10 | 19 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7316 | 6572 | 10 | 20 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7317 | 6573 | 10 | 21 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7318 | 6574 | 10 | 22 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7319 | 6575 | 10 | 23 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7320 | 6576 | 10 | 24 | 274 | 43374 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7321 | 6577 | 10 | 1 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7322 | 6578 | 10 | 2 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7323 | 6579 | 10 | 3 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7324 | 6580 | 10 | 4 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7325 | 6581 | 10 | 5 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7326 | 6582 | 10 | 6 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7327 | 6583 | 10 | 7 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7328 | 6584 | 10 | 8 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7329 | 6585 | 10 | 9 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7330 | 6586 | 10 | 10 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7331 | 6587 | 10 | 11 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7332 | 6588 | 10 | 12 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7333 | 6589 | 10 | 13 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7334 | 6590 | 10 | 14 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7335 | 6591 | 10 | 15 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7336 | 6592 | 10 | 16 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7337 | 6593 | 10 | 17 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7338 | 6594 | 10 | 18 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7339 | 6595 | 10 | 19 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7340 | 6596 | 10 | 20 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7341 | 6597 | 10 | 21 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7342 | 6598 | 10 | 22 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7343 | 6599 | 10 | 23 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7344 | 6600 | 10 | 24 | 275 | 43375 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7345 | 6601 | 10 | 1 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7346 | 6602 | 10 | 2 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7347 | 6603 | 10 | 3 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7348 | 6604 | 10 | 4 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7349 | 6605 | 10 | 5 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7350 | 6606 | 10 | 6 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7351 | 6607 | 10 | 7 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7352 | 6608 | 10 | 8 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7353 | 6609 | 10 | 9 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7354 | 6610 | 10 | 10 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7355 | 6611 | 10 | 11 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7356 | 6612 | 10 | 12 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7357 | 6613 | 10 | 13 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7358 | 6614 | 10 | 14 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7359 | 6615 | 10 | 15 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7360 | 6616 | 10 | 16 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7361 | 6617 | 10 | 17 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7362 | 6618 | 10 | 18 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7363 | 6619 | 10 | 19 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7364 | 6620 | 10 | 20 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7365 | 6621 | 10 | 21 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7366 | 6622 | 10 | 22 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7367 | 6623 | 10 | 23 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7368 | 6624 | 10 | 24 | 276 | 43376 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7369 | 6625 | 10 | 1 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7370 | 6626 | 10 | 2 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7371 | 6627 | 10 | 3 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7372 | 6628 | 10 | 4 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7373 | 6629 | 10 | 5 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7374 | 6630 | 10 | 6 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7375 | 6631 | 10 | 7 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7376 | 6632 | 10 | 8 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7377 | 6633 | 10 | 9 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7378 | 6634 | 10 | 10 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7379 | 6635 | 10 | 11 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7380 | 6636 | 10 | 12 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7381 | 6637 | 10 | 13 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7382 | 6638 | 10 | 14 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7383 | 6639 | 10 | 15 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7384 | 6640 | 10 | 16 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7385 | 6641 | 10 | 17 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7386 | 6642 | 10 | 18 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7387 | 6643 | 10 | 19 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7388 | 6644 | 10 | 20 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7389 | 6645 | 10 | 21 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7390 | 6646 | 10 | 22 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7391 | 6647 | 10 | 23 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7392 | 6648 | 10 | 24 | 277 | 43377 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7393 | 6649 | 10 | 1 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7394 | 6650 | 10 | 2 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7395 | 6651 | 10 | 3 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7396 | 6652 | 10 | 4 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7397 | 6653 | 10 | 5 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7398 | 6654 | 10 | 6 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7399 | 6655 | 10 | 7 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7400 | 6656 | 10 | 8 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7401 | 6657 | 10 | 9 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7402 | 6658 | 10 | 10 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7403 | 6659 | 10 | 11 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7404 | 6660 | 10 | 12 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7405 | 6661 | 10 | 13 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7406 | 6662 | 10 | 14 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7407 | 6663 | 10 | 15 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7408 | 6664 | 10 | 16 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7409 | 6665 | 10 | 17 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7410 | 6666 | 10 | 18 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7411 | 6667 | 10 | 19 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7412 | 6668 | 10 | 20 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7413 | 6669 | 10 | 21 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7414 | 6670 | 10 | 22 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7415 | 6671 | 10 | 23 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7416 | 6672 | 10 | 24 | 278 | 43378 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7417 | 6673 | 10 | 1 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7418 | 6674 | 10 | 2 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7419 | 6675 | 10 | 3 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7420 | 6676 | 10 | 4 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7421 | 6677 | 10 | 5 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7422 | 6678 | 10 | 6 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7423 | 6679 | 10 | 7 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7424 | 6680 | 10 | 8 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7425 | 6681 | 10 | 9 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7426 | 6682 | 10 | 10 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7427 | 6683 | 10 | 11 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7428 | 6684 | 10 | 12 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7429 | 6685 | 10 | 13 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7430 | 6686 | 10 | 14 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7431 | 6687 | 10 | 15 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7432 | 6688 | 10 | 16 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7433 | 6689 | 10 | 17 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7434 | 6690 | 10 | 18 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7435 | 6691 | 10 | 19 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7436 | 6692 | 10 | 20 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7437 | 6693 | 10 | 21 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7438 | 6694 | 10 | 22 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7439 | 6695 | 10 | 23 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7440 | 6696 | 10 | 24 | 279 | 43379 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7441 | 6697 | 10 | 1 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7442 | 6698 | 10 | 2 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7443 | 6699 | 10 | 3 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7444 | 6700 | 10 | 4 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7445 | 6701 | 10 | 5 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7446 | 6702 | 10 | 6 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7447 | 6703 | 10 | 7 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7448 | 6704 | 10 | 8 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7449 | 6705 | 10 | 9 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7450 | 6706 | 10 | 10 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7451 | 6707 | 10 | 11 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7452 | 6708 | 10 | 12 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7453 | 6709 | 10 | 13 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7454 | 6710 | 10 | 14 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7455 | 6711 | 10 | 15 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7456 | 6712 | 10 | 16 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7457 | 6713 | 10 | 17 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7458 | 6714 | 10 | 18 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7459 | 6715 | 10 | 19 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7460 | 6716 | 10 | 20 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7461 | 6717 | 10 | 21 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7462 | 6718 | 10 | 22 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7463 | 6719 | 10 | 23 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7464 | 6720 | 10 | 24 | 280 | 43380 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7465 | 6721 | 10 | 1 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7466 | 6722 | 10 | 2 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7467 | 6723 | 10 | 3 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7468 | 6724 | 10 | 4 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7469 | 6725 | 10 | 5 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7470 | 6726 | 10 | 6 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7471 | 6727 | 10 | 7 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7472 | 6728 | 10 | 8 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7473 | 6729 | 10 | 9 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7474 | 6730 | 10 | 10 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7475 | 6731 | 10 | 11 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7476 | 6732 | 10 | 12 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7477 | 6733 | 10 | 13 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7478 | 6734 | 10 | 14 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7479 | 6735 | 10 | 15 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7480 | 6736 | 10 | 16 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7481 | 6737 | 10 | 17 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7482 | 6738 | 10 | 18 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7483 | 6739 | 10 | 19 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7484 | 6740 | 10 | 20 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7485 | 6741 | 10 | 21 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7486 | 6742 | 10 | 22 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7487 | 6743 | 10 | 23 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7488 | 6744 | 10 | 24 | 281 | 43381 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7489 | 6745 | 10 | 1 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7490 | 6746 | 10 | 2 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7491 | 6747 | 10 | 3 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7492 | 6748 | 10 | 4 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7493 | 6749 | 10 | 5 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7494 | 6750 | 10 | 6 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7495 | 6751 | 10 | 7 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7496 | 6752 | 10 | 8 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7497 | 6753 | 10 | 9 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7498 | 6754 | 10 | 10 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7499 | 6755 | 10 | 11 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7500 | 6756 | 10 | 12 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7501 | 6757 | 10 | 13 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7502 | 6758 | 10 | 14 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7503 | 6759 | 10 | 15 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7504 | 6760 | 10 | 16 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7505 | 6761 | 10 | 17 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7506 | 6762 | 10 | 18 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7507 | 6763 | 10 | 19 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7508 | 6764 | 10 | 20 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7509 | 6765 | 10 | 21 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7510 | 6766 | 10 | 22 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7511 | 6767 | 10 | 23 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7512 | 6768 | 10 | 24 | 282 | 43382 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7513 | 6769 | 10 | 1 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7514 | 6770 | 10 | 2 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7515 | 6771 | 10 | 3 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7516 | 6772 | 10 | 4 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7517 | 6773 | 10 | 5 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7518 | 6774 | 10 | 6 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7519 | 6775 | 10 | 7 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7520 | 6776 | 10 | 8 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7521 | 6777 | 10 | 9 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7522 | 6778 | 10 | 10 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7523 | 6779 | 10 | 11 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7524 | 6780 | 10 | 12 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7525 | 6781 | 10 | 13 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7526 | 6782 | 10 | 14 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7527 | 6783 | 10 | 15 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7528 | 6784 | 10 | 16 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7529 | 6785 | 10 | 17 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7530 | 6786 | 10 | 18 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7531 | 6787 | 10 | 19 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7532 | 6788 | 10 | 20 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7533 | 6789 | 10 | 21 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7534 | 6790 | 10 | 22 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7535 | 6791 | 10 | 23 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7536 | 6792 | 10 | 24 | 283 | 43383 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7537 | 6793 | 10 | 1 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7538 | 6794 | 10 | 2 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7539 | 6795 | 10 | 3 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7540 | 6796 | 10 | 4 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7541 | 6797 | 10 | 5 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7542 | 6798 | 10 | 6 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7543 | 6799 | 10 | 7 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7544 | 6800 | 10 | 8 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7545 | 6801 | 10 | 9 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7546 | 6802 | 10 | 10 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7547 | 6803 | 10 | 11 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7548 | 6804 | 10 | 12 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7549 | 6805 | 10 | 13 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7550 | 6806 | 10 | 14 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7551 | 6807 | 10 | 15 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7552 | 6808 | 10 | 16 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7553 | 6809 | 10 | 17 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7554 | 6810 | 10 | 18 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7555 | 6811 | 10 | 19 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7556 | 6812 | 10 | 20 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7557 | 6813 | 10 | 21 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7558 | 6814 | 10 | 22 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7559 | 6815 | 10 | 23 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7560 | 6816 | 10 | 24 | 284 | 43384 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7561 | 6817 | 10 | 1 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7562 | 6818 | 10 | 2 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7563 | 6819 | 10 | 3 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7564 | 6820 | 10 | 4 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7565 | 6821 | 10 | 5 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7566 | 6822 | 10 | 6 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7567 | 6823 | 10 | 7 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7568 | 6824 | 10 | 8 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7569 | 6825 | 10 | 9 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7570 | 6826 | 10 | 10 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7571 | 6827 | 10 | 11 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7572 | 6828 | 10 | 12 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7573 | 6829 | 10 | 13 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7574 | 6830 | 10 | 14 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7575 | 6831 | 10 | 15 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7576 | 6832 | 10 | 16 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7577 | 6833 | 10 | 17 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7578 | 6834 | 10 | 18 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7579 | 6835 | 10 | 19 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7580 | 6836 | 10 | 20 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7581 | 6837 | 10 | 21 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7582 | 6838 | 10 | 22 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7583 | 6839 | 10 | 23 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7584 | 6840 | 10 | 24 | 285 | 43385 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7585 | 6841 | 10 | 1 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7586 | 6842 | 10 | 2 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7587 | 6843 | 10 | 3 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7588 | 6844 | 10 | 4 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7589 | 6845 | 10 | 5 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7590 | 6846 | 10 | 6 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7591 | 6847 | 10 | 7 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7592 | 6848 | 10 | 8 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7593 | 6849 | 10 | 9 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7594 | 6850 | 10 | 10 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7595 | 6851 | 10 | 11 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7596 | 6852 | 10 | 12 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7597 | 6853 | 10 | 13 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7598 | 6854 | 10 | 14 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7599 | 6855 | 10 | 15 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7600 | 6856 | 10 | 16 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7601 | 6857 | 10 | 17 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7602 | 6858 | 10 | 18 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7603 | 6859 | 10 | 19 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7604 | 6860 | 10 | 20 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7605 | 6861 | 10 | 21 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7606 | 6862 | 10 | 22 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7607 | 6863 | 10 | 23 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7608 | 6864 | 10 | 24 | 286 | 43386 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7609 | 6865 | 10 | 1 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7610 | 6866 | 10 | 2 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7611 | 6867 | 10 | 3 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7612 | 6868 | 10 | 4 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7613 | 6869 | 10 | 5 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7614 | 6870 | 10 | 6 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7615 | 6871 | 10 | 7 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7616 | 6872 | 10 | 8 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7617 | 6873 | 10 | 9 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7618 | 6874 | 10 | 10 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7619 | 6875 | 10 | 11 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7620 | 6876 | 10 | 12 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7621 | 6877 | 10 | 13 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7622 | 6878 | 10 | 14 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7623 | 6879 | 10 | 15 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7624 | 6880 | 10 | 16 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7625 | 6881 | 10 | 17 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7626 | 6882 | 10 | 18 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7627 | 6883 | 10 | 19 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7628 | 6884 | 10 | 20 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7629 | 6885 | 10 | 21 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7630 | 6886 | 10 | 22 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7631 | 6887 | 10 | 23 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7632 | 6888 | 10 | 24 | 287 | 43387 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7633 | 6889 | 10 | 1 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7634 | 6890 | 10 | 2 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7635 | 6891 | 10 | 3 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7636 | 6892 | 10 | 4 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7637 | 6893 | 10 | 5 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7638 | 6894 | 10 | 6 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7639 | 6895 | 10 | 7 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7640 | 6896 | 10 | 8 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7641 | 6897 | 10 | 9 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7642 | 6898 | 10 | 10 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7643 | 6899 | 10 | 11 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7644 | 6900 | 10 | 12 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7645 | 6901 | 10 | 13 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7646 | 6902 | 10 | 14 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7647 | 6903 | 10 | 15 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7648 | 6904 | 10 | 16 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7649 | 6905 | 10 | 17 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7650 | 6906 | 10 | 18 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7651 | 6907 | 10 | 19 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7652 | 6908 | 10 | 20 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7653 | 6909 | 10 | 21 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7654 | 6910 | 10 | 22 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7655 | 6911 | 10 | 23 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7656 | 6912 | 10 | 24 | 288 | 43388 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7657 | 6913 | 10 | 1 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7658 | 6914 | 10 | 2 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7659 | 6915 | 10 | 3 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7660 | 6916 | 10 | 4 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7661 | 6917 | 10 | 5 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7662 | 6918 | 10 | 6 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7663 | 6919 | 10 | 7 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7664 | 6920 | 10 | 8 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7665 | 6921 | 10 | 9 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7666 | 6922 | 10 | 10 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7667 | 6923 | 10 | 11 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7668 | 6924 | 10 | 12 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7669 | 6925 | 10 | 13 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7670 | 6926 | 10 | 14 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7671 | 6927 | 10 | 15 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7672 | 6928 | 10 | 16 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7673 | 6929 | 10 | 17 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7674 | 6930 | 10 | 18 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7675 | 6931 | 10 | 19 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7676 | 6932 | 10 | 20 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7677 | 6933 | 10 | 21 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7678 | 6934 | 10 | 22 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7679 | 6935 | 10 | 23 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7680 | 6936 | 10 | 24 | 289 | 43389 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7681 | 6937 | 10 | 1 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7682 | 6938 | 10 | 2 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7683 | 6939 | 10 | 3 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7684 | 6940 | 10 | 4 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7685 | 6941 | 10 | 5 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7686 | 6942 | 10 | 6 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7687 | 6943 | 10 | 7 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7688 | 6944 | 10 | 8 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7689 | 6945 | 10 | 9 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7690 | 6946 | 10 | 10 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7691 | 6947 | 10 | 11 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7692 | 6948 | 10 | 12 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7693 | 6949 | 10 | 13 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7694 | 6950 | 10 | 14 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7695 | 6951 | 10 | 15 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7696 | 6952 | 10 | 16 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7697 | 6953 | 10 | 17 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7698 | 6954 | 10 | 18 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7699 | 6955 | 10 | 19 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7700 | 6956 | 10 | 20 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7701 | 6957 | 10 | 21 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7702 | 6958 | 10 | 22 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7703 | 6959 | 10 | 23 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7704 | 6960 | 10 | 24 | 290 | 43390 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7705 | 6961 | 10 | 1 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7706 | 6962 | 10 | 2 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7707 | 6963 | 10 | 3 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7708 | 6964 | 10 | 4 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7709 | 6965 | 10 | 5 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7710 | 6966 | 10 | 6 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7711 | 6967 | 10 | 7 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7712 | 6968 | 10 | 8 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7713 | 6969 | 10 | 9 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7714 | 6970 | 10 | 10 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7715 | 6971 | 10 | 11 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7716 | 6972 | 10 | 12 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7717 | 6973 | 10 | 13 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7718 | 6974 | 10 | 14 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7719 | 6975 | 10 | 15 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7720 | 6976 | 10 | 16 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7721 | 6977 | 10 | 17 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7722 | 6978 | 10 | 18 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7723 | 6979 | 10 | 19 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7724 | 6980 | 10 | 20 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7725 | 6981 | 10 | 21 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7726 | 6982 | 10 | 22 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7727 | 6983 | 10 | 23 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7728 | 6984 | 10 | 24 | 291 | 43391 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7729 | 6985 | 10 | 1 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7730 | 6986 | 10 | 2 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7731 | 6987 | 10 | 3 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7732 | 6988 | 10 | 4 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7733 | 6989 | 10 | 5 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7734 | 6990 | 10 | 6 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7735 | 6991 | 10 | 7 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7736 | 6992 | 10 | 8 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7737 | 6993 | 10 | 9 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7738 | 6994 | 10 | 10 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7739 | 6995 | 10 | 11 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7740 | 6996 | 10 | 12 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7741 | 6997 | 10 | 13 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7742 | 6998 | 10 | 14 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7743 | 6999 | 10 | 15 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7744 | 7000 | 10 | 16 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7745 | 7001 | 10 | 17 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7746 | 7002 | 10 | 18 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7747 | 7003 | 10 | 19 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7748 | 7004 | 10 | 20 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7749 | 7005 | 10 | 21 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7750 | 7006 | 10 | 22 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7751 | 7007 | 10 | 23 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7752 | 7008 | 10 | 24 | 292 | 43392 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7753 | 7009 | 10 | 1 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7754 | 7010 | 10 | 2 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7755 | 7011 | 10 | 3 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7756 | 7012 | 10 | 4 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7757 | 7013 | 10 | 5 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7758 | 7014 | 10 | 6 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7759 | 7015 | 10 | 7 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7760 | 7016 | 10 | 8 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7761 | 7017 | 10 | 9 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7762 | 7018 | 10 | 10 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7763 | 7019 | 10 | 11 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7764 | 7020 | 10 | 12 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7765 | 7021 | 10 | 13 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7766 | 7022 | 10 | 14 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7767 | 7023 | 10 | 15 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7768 | 7024 | 10 | 16 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7769 | 7025 | 10 | 17 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7770 | 7026 | 10 | 18 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7771 | 7027 | 10 | 19 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7772 | 7028 | 10 | 20 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7773 | 7029 | 10 | 21 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7774 | 7030 | 10 | 22 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7775 | 7031 | 10 | 23 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7776 | 7032 | 10 | 24 | 293 | 43393 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7777 | 7033 | 10 | 1 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7778 | 7034 | 10 | 2 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7779 | 7035 | 10 | 3 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7780 | 7036 | 10 | 4 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7781 | 7037 | 10 | 5 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7782 | 7038 | 10 | 6 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7783 | 7039 | 10 | 7 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7784 | 7040 | 10 | 8 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7785 | 7041 | 10 | 9 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7786 | 7042 | 10 | 10 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7787 | 7043 | 10 | 11 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7788 | 7044 | 10 | 12 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7789 | 7045 | 10 | 13 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7790 | 7046 | 10 | 14 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7791 | 7047 | 10 | 15 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7792 | 7048 | 10 | 16 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7793 | 7049 | 10 | 17 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7794 | 7050 | 10 | 18 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7795 | 7051 | 10 | 19 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7796 | 7052 | 10 | 20 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7797 | 7053 | 10 | 21 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7798 | 7054 | 10 | 22 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7799 | 7055 | 10 | 23 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7800 | 7056 | 10 | 24 | 294 | 43394 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7801 | 7057 | 10 | 1 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7802 | 7058 | 10 | 2 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7803 | 7059 | 10 | 3 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7804 | 7060 | 10 | 4 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7805 | 7061 | 10 | 5 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7806 | 7062 | 10 | 6 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7807 | 7063 | 10 | 7 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7808 | 7064 | 10 | 8 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7809 | 7065 | 10 | 9 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7810 | 7066 | 10 | 10 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7811 | 7067 | 10 | 11 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7812 | 7068 | 10 | 12 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7813 | 7069 | 10 | 13 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7814 | 7070 | 10 | 14 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7815 | 7071 | 10 | 15 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7816 | 7072 | 10 | 16 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7817 | 7073 | 10 | 17 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7818 | 7074 | 10 | 18 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7819 | 7075 | 10 | 19 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7820 | 7076 | 10 | 20 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7821 | 7077 | 10 | 21 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7822 | 7078 | 10 | 22 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7823 | 7079 | 10 | 23 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7824 | 7080 | 10 | 24 | 295 | 43395 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7825 | 7081 | 10 | 1 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7826 | 7082 | 10 | 2 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7827 | 7083 | 10 | 3 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7828 | 7084 | 10 | 4 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7829 | 7085 | 10 | 5 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7830 | 7086 | 10 | 6 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7831 | 7087 | 10 | 7 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7832 | 7088 | 10 | 8 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7833 | 7089 | 10 | 9 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7834 | 7090 | 10 | 10 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7835 | 7091 | 10 | 11 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7836 | 7092 | 10 | 12 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7837 | 7093 | 10 | 13 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7838 | 7094 | 10 | 14 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7839 | 7095 | 10 | 15 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7840 | 7096 | 10 | 16 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7841 | 7097 | 10 | 17 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7842 | 7098 | 10 | 18 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7843 | 7099 | 10 | 19 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7844 | 7100 | 10 | 20 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7845 | 7101 | 10 | 21 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7846 | 7102 | 10 | 22 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7847 | 7103 | 10 | 23 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7848 | 7104 | 10 | 24 | 296 | 43396 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7849 | 7105 | 10 | 1 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7850 | 7106 | 10 | 2 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7851 | 7107 | 10 | 3 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7852 | 7108 | 10 | 4 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7853 | 7109 | 10 | 5 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7854 | 7110 | 10 | 6 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7855 | 7111 | 10 | 7 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7856 | 7112 | 10 | 8 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7857 | 7113 | 10 | 9 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7858 | 7114 | 10 | 10 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7859 | 7115 | 10 | 11 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7860 | 7116 | 10 | 12 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7861 | 7117 | 10 | 13 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7862 | 7118 | 10 | 14 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7863 | 7119 | 10 | 15 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7864 | 7120 | 10 | 16 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7865 | 7121 | 10 | 17 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7866 | 7122 | 10 | 18 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7867 | 7123 | 10 | 19 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7868 | 7124 | 10 | 20 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7869 | 7125 | 10 | 21 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7870 | 7126 | 10 | 22 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7871 | 7127 | 10 | 23 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7872 | 7128 | 10 | 24 | 297 | 43397 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7873 | 7129 | 10 | 1 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7874 | 7130 | 10 | 2 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7875 | 7131 | 10 | 3 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7876 | 7132 | 10 | 4 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7877 | 7133 | 10 | 5 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7878 | 7134 | 10 | 6 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7879 | 7135 | 10 | 7 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7880 | 7136 | 10 | 8 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7881 | 7137 | 10 | 9 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7882 | 7138 | 10 | 10 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7883 | 7139 | 10 | 11 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7884 | 7140 | 10 | 12 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7885 | 7141 | 10 | 13 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7886 | 7142 | 10 | 14 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7887 | 7143 | 10 | 15 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7888 | 7144 | 10 | 16 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7889 | 7145 | 10 | 17 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7890 | 7146 | 10 | 18 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7891 | 7147 | 10 | 19 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7892 | 7148 | 10 | 20 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7893 | 7149 | 10 | 21 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7894 | 7150 | 10 | 22 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7895 | 7151 | 10 | 23 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7896 | 7152 | 10 | 24 | 298 | 43398 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7897 | 7153 | 10 | 1 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7898 | 7154 | 10 | 2 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7899 | 7155 | 10 | 3 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7900 | 7156 | 10 | 4 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7901 | 7157 | 10 | 5 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7902 | 7158 | 10 | 6 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7903 | 7159 | 10 | 7 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7904 | 7160 | 10 | 8 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7905 | 7161 | 10 | 9 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7906 | 7162 | 10 | 10 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7907 | 7163 | 10 | 11 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7908 | 7164 | 10 | 12 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7909 | 7165 | 10 | 13 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7910 | 7166 | 10 | 14 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7911 | 7167 | 10 | 15 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7912 | 7168 | 10 | 16 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7913 | 7169 | 10 | 17 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7914 | 7170 | 10 | 18 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7915 | 7171 | 10 | 19 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7916 | 7172 | 10 | 20 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7917 | 7173 | 10 | 21 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7918 | 7174 | 10 | 22 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7919 | 7175 | 10 | 23 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7920 | 7176 | 10 | 24 | 299 | 43399 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7921 | 7177 | 10 | 1 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7922 | 7178 | 10 | 2 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7923 | 7179 | 10 | 3 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7924 | 7180 | 10 | 4 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7925 | 7181 | 10 | 5 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7926 | 7182 | 10 | 6 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7927 | 7183 | 10 | 7 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7928 | 7184 | 10 | 8 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7929 | 7185 | 10 | 9 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7930 | 7186 | 10 | 10 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7931 | 7187 | 10 | 11 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7932 | 7188 | 10 | 12 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7933 | 7189 | 10 | 13 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7934 | 7190 | 10 | 14 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7935 | 7191 | 10 | 15 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7936 | 7192 | 10 | 16 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7937 | 7193 | 10 | 17 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7938 | 7194 | 10 | 18 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7939 | 7195 | 10 | 19 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7940 | 7196 | 10 | 20 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7941 | 7197 | 10 | 21 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7942 | 7198 | 10 | 22 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7943 | 7199 | 10 | 23 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7944 | 7200 | 10 | 24 | 300 | 43400 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7945 | 7201 | 10 | 1 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7946 | 7202 | 10 | 2 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7947 | 7203 | 10 | 3 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7948 | 7204 | 10 | 4 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7949 | 7205 | 10 | 5 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7950 | 7206 | 10 | 6 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7951 | 7207 | 10 | 7 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7952 | 7208 | 10 | 8 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7953 | 7209 | 10 | 9 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7954 | 7210 | 10 | 10 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7955 | 7211 | 10 | 11 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7956 | 7212 | 10 | 12 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7957 | 7213 | 10 | 13 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7958 | 7214 | 10 | 14 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7959 | 7215 | 10 | 15 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7960 | 7216 | 10 | 16 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7961 | 7217 | 10 | 17 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7962 | 7218 | 10 | 18 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7963 | 7219 | 10 | 19 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7964 | 7220 | 10 | 20 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7965 | 7221 | 10 | 21 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7966 | 7222 | 10 | 22 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7967 | 7223 | 10 | 23 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7968 | 7224 | 10 | 24 | 301 | 43401 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7969 | 7225 | 10 | 1 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7970 | 7226 | 10 | 2 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7971 | 7227 | 10 | 3 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7972 | 7228 | 10 | 4 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7973 | 7229 | 10 | 5 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7974 | 7230 | 10 | 6 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7975 | 7231 | 10 | 7 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7976 | 7232 | 10 | 8 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7977 | 7233 | 10 | 9 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7978 | 7234 | 10 | 10 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7979 | 7235 | 10 | 11 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7980 | 7236 | 10 | 12 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7981 | 7237 | 10 | 13 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7982 | 7238 | 10 | 14 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7983 | 7239 | 10 | 15 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7984 | 7240 | 10 | 16 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7985 | 7241 | 10 | 17 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7986 | 7242 | 10 | 18 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7987 | 7243 | 10 | 19 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7988 | 7244 | 10 | 20 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7989 | 7245 | 10 | 21 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7990 | 7246 | 10 | 22 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7991 | 7247 | 10 | 23 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7992 | 7248 | 10 | 24 | 302 | 43402 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7993 | 7249 | 10 | 1 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7994 | 7250 | 10 | 2 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7995 | 7251 | 10 | 3 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7996 | 7252 | 10 | 4 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7997 | 7253 | 10 | 5 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7998 | 7254 | 10 | 6 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 7999 | 7255 | 10 | 7 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8000 | 7256 | 10 | 8 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8001 | 7257 | 10 | 9 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8002 | 7258 | 10 | 10 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8003 | 7259 | 10 | 11 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8004 | 7260 | 10 | 12 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8005 | 7261 | 10 | 13 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8006 | 7262 | 10 | 14 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8007 | 7263 | 10 | 15 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8008 | 7264 | 10 | 16 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8009 | 7265 | 10 | 17 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8010 | 7266 | 10 | 18 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8011 | 7267 | 10 | 19 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8012 | 7268 | 10 | 20 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8013 | 7269 | 10 | 21 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8014 | 7270 | 10 | 22 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8015 | 7271 | 10 | 23 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8016 | 7272 | 10 | 24 | 303 | 43403 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8017 | 7273 | 10 | 1 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8018 | 7274 | 10 | 2 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8019 | 7275 | 10 | 3 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8020 | 7276 | 10 | 4 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8021 | 7277 | 10 | 5 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8022 | 7278 | 10 | 6 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8023 | 7279 | 10 | 7 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8024 | 7280 | 10 | 8 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8025 | 7281 | 10 | 9 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8026 | 7282 | 10 | 10 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8027 | 7283 | 10 | 11 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8028 | 7284 | 10 | 12 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8029 | 7285 | 10 | 13 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8030 | 7286 | 10 | 14 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8031 | 7287 | 10 | 15 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8032 | 7288 | 10 | 16 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8033 | 7289 | 10 | 17 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8034 | 7290 | 10 | 18 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8035 | 7291 | 10 | 19 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8036 | 7292 | 10 | 20 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8037 | 7293 | 10 | 21 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8038 | 7294 | 10 | 22 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8039 | 7295 | 10 | 23 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8040 | 7296 | 10 | 24 | 304 | 43404 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8041 | 7297 | 11 | 1 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8042 | 7298 | 11 | 2 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8043 | 7299 | 11 | 3 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8044 | 7300 | 11 | 4 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8045 | 7301 | 11 | 5 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8046 | 7302 | 11 | 6 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8047 | 7303 | 11 | 7 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8048 | 7304 | 11 | 8 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8049 | 7305 | 11 | 9 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8050 | 7306 | 11 | 10 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8051 | 7307 | 11 | 11 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8052 | 7308 | 11 | 12 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8053 | 7309 | 11 | 13 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8054 | 7310 | 11 | 14 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8055 | 7311 | 11 | 15 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8056 | 7312 | 11 | 16 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8057 | 7313 | 11 | 17 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8058 | 7314 | 11 | 18 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8059 | 7315 | 11 | 19 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8060 | 7316 | 11 | 20 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8061 | 7317 | 11 | 21 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8062 | 7318 | 11 | 22 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8063 | 7319 | 11 | 23 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8064 | 7320 | 11 | 24 | 305 | 43405 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8065 | 7321 | 11 | 1 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8066 | 7322 | 11 | 2 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8067 | 7323 | 11 | 3 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8068 | 7324 | 11 | 4 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8069 | 7325 | 11 | 5 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8070 | 7326 | 11 | 6 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8071 | 7327 | 11 | 7 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8072 | 7328 | 11 | 8 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8073 | 7329 | 11 | 9 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8074 | 7330 | 11 | 10 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8075 | 7331 | 11 | 11 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8076 | 7332 | 11 | 12 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8077 | 7333 | 11 | 13 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8078 | 7334 | 11 | 14 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8079 | 7335 | 11 | 15 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8080 | 7336 | 11 | 16 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8081 | 7337 | 11 | 17 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8082 | 7338 | 11 | 18 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8083 | 7339 | 11 | 19 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8084 | 7340 | 11 | 20 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8085 | 7341 | 11 | 21 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8086 | 7342 | 11 | 22 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8087 | 7343 | 11 | 23 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8088 | 7344 | 11 | 24 | 306 | 43406 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8089 | 7345 | 11 | 1 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8090 | 7346 | 11 | 2 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8091 | 7347 | 11 | 3 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8092 | 7348 | 11 | 4 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8093 | 7349 | 11 | 5 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8094 | 7350 | 11 | 6 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8095 | 7351 | 11 | 7 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8096 | 7352 | 11 | 8 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8097 | 7353 | 11 | 9 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8098 | 7354 | 11 | 10 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8099 | 7355 | 11 | 11 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8100 | 7356 | 11 | 12 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8101 | 7357 | 11 | 13 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8102 | 7358 | 11 | 14 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8103 | 7359 | 11 | 15 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8104 | 7360 | 11 | 16 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8105 | 7361 | 11 | 17 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8106 | 7362 | 11 | 18 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8107 | 7363 | 11 | 19 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8108 | 7364 | 11 | 20 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8109 | 7365 | 11 | 21 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8110 | 7366 | 11 | 22 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8111 | 7367 | 11 | 23 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8112 | 7368 | 11 | 24 | 307 | 43407 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8113 | 7369 | 11 | 1 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8114 | 7370 | 11 | 2 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8115 | 7371 | 11 | 3 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8116 | 7372 | 11 | 4 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8117 | 7373 | 11 | 5 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8118 | 7374 | 11 | 6 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8119 | 7375 | 11 | 7 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8120 | 7376 | 11 | 8 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8121 | 7377 | 11 | 9 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8122 | 7378 | 11 | 10 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8123 | 7379 | 11 | 11 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8124 | 7380 | 11 | 12 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8125 | 7381 | 11 | 13 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8126 | 7382 | 11 | 14 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8127 | 7383 | 11 | 15 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8128 | 7384 | 11 | 16 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8129 | 7385 | 11 | 17 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8130 | 7386 | 11 | 18 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8131 | 7387 | 11 | 19 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8132 | 7388 | 11 | 20 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8133 | 7389 | 11 | 21 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8134 | 7390 | 11 | 22 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8135 | 7391 | 11 | 23 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8136 | 7392 | 11 | 24 | 308 | 43408 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8137 | 7393 | 11 | 1 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8138 | 7394 | 11 | 2 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8139 | 7395 | 11 | 3 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8140 | 7396 | 11 | 4 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8141 | 7397 | 11 | 5 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8142 | 7398 | 11 | 6 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8143 | 7399 | 11 | 7 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8144 | 7400 | 11 | 8 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8145 | 7401 | 11 | 9 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8146 | 7402 | 11 | 10 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8147 | 7403 | 11 | 11 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8148 | 7404 | 11 | 12 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8149 | 7405 | 11 | 13 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8150 | 7406 | 11 | 14 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8151 | 7407 | 11 | 15 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8152 | 7408 | 11 | 16 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8153 | 7409 | 11 | 17 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8154 | 7410 | 11 | 18 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8155 | 7411 | 11 | 19 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8156 | 7412 | 11 | 20 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8157 | 7413 | 11 | 21 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8158 | 7414 | 11 | 22 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8159 | 7415 | 11 | 23 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8160 | 7416 | 11 | 24 | 309 | 43409 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8161 | 7417 | 11 | 1 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8162 | 7418 | 11 | 2 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8163 | 7419 | 11 | 3 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8164 | 7420 | 11 | 4 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8165 | 7421 | 11 | 5 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8166 | 7422 | 11 | 6 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8167 | 7423 | 11 | 7 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8168 | 7424 | 11 | 8 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8169 | 7425 | 11 | 9 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8170 | 7426 | 11 | 10 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8171 | 7427 | 11 | 11 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8172 | 7428 | 11 | 12 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8173 | 7429 | 11 | 13 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8174 | 7430 | 11 | 14 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8175 | 7431 | 11 | 15 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8176 | 7432 | 11 | 16 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8177 | 7433 | 11 | 17 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8178 | 7434 | 11 | 18 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8179 | 7435 | 11 | 19 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8180 | 7436 | 11 | 20 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8181 | 7437 | 11 | 21 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8182 | 7438 | 11 | 22 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8183 | 7439 | 11 | 23 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8184 | 7440 | 11 | 24 | 310 | 43410 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8185 | 7441 | 11 | 1 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8186 | 7442 | 11 | 2 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8187 | 7443 | 11 | 3 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8188 | 7444 | 11 | 4 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8189 | 7445 | 11 | 5 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8190 | 7446 | 11 | 6 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8191 | 7447 | 11 | 7 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8192 | 7448 | 11 | 8 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8193 | 7449 | 11 | 9 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8194 | 7450 | 11 | 10 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8195 | 7451 | 11 | 11 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8196 | 7452 | 11 | 12 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8197 | 7453 | 11 | 13 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8198 | 7454 | 11 | 14 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8199 | 7455 | 11 | 15 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8200 | 7456 | 11 | 16 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8201 | 7457 | 11 | 17 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8202 | 7458 | 11 | 18 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8203 | 7459 | 11 | 19 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8204 | 7460 | 11 | 20 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8205 | 7461 | 11 | 21 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8206 | 7462 | 11 | 22 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8207 | 7463 | 11 | 23 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8208 | 7464 | 11 | 24 | 311 | 43411 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8209 | 7465 | 11 | 1 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8210 | 7466 | 11 | 2 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8211 | 7467 | 11 | 3 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8212 | 7468 | 11 | 4 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8213 | 7469 | 11 | 5 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8214 | 7470 | 11 | 6 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8215 | 7471 | 11 | 7 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8216 | 7472 | 11 | 8 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8217 | 7473 | 11 | 9 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8218 | 7474 | 11 | 10 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8219 | 7475 | 11 | 11 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8220 | 7476 | 11 | 12 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8221 | 7477 | 11 | 13 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8222 | 7478 | 11 | 14 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8223 | 7479 | 11 | 15 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8224 | 7480 | 11 | 16 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8225 | 7481 | 11 | 17 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8226 | 7482 | 11 | 18 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8227 | 7483 | 11 | 19 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8228 | 7484 | 11 | 20 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8229 | 7485 | 11 | 21 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8230 | 7486 | 11 | 22 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8231 | 7487 | 11 | 23 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8232 | 7488 | 11 | 24 | 312 | 43412 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8233 | 7489 | 11 | 1 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8234 | 7490 | 11 | 2 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8235 | 7491 | 11 | 3 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8236 | 7492 | 11 | 4 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8237 | 7493 | 11 | 5 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8238 | 7494 | 11 | 6 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8239 | 7495 | 11 | 7 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8240 | 7496 | 11 | 8 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8241 | 7497 | 11 | 9 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8242 | 7498 | 11 | 10 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8243 | 7499 | 11 | 11 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8244 | 7500 | 11 | 12 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8245 | 7501 | 11 | 13 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8246 | 7502 | 11 | 14 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8247 | 7503 | 11 | 15 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8248 | 7504 | 11 | 16 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8249 | 7505 | 11 | 17 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8250 | 7506 | 11 | 18 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8251 | 7507 | 11 | 19 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8252 | 7508 | 11 | 20 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8253 | 7509 | 11 | 21 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8254 | 7510 | 11 | 22 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8255 | 7511 | 11 | 23 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8256 | 7512 | 11 | 24 | 313 | 43413 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8257 | 7513 | 11 | 1 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8258 | 7514 | 11 | 2 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8259 | 7515 | 11 | 3 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8260 | 7516 | 11 | 4 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8261 | 7517 | 11 | 5 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8262 | 7518 | 11 | 6 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8263 | 7519 | 11 | 7 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8264 | 7520 | 11 | 8 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8265 | 7521 | 11 | 9 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8266 | 7522 | 11 | 10 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8267 | 7523 | 11 | 11 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8268 | 7524 | 11 | 12 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8269 | 7525 | 11 | 13 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8270 | 7526 | 11 | 14 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8271 | 7527 | 11 | 15 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8272 | 7528 | 11 | 16 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8273 | 7529 | 11 | 17 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8274 | 7530 | 11 | 18 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8275 | 7531 | 11 | 19 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8276 | 7532 | 11 | 20 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8277 | 7533 | 11 | 21 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8278 | 7534 | 11 | 22 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8279 | 7535 | 11 | 23 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8280 | 7536 | 11 | 24 | 314 | 43414 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8281 | 7537 | 11 | 1 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8282 | 7538 | 11 | 2 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8283 | 7539 | 11 | 3 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8284 | 7540 | 11 | 4 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8285 | 7541 | 11 | 5 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8286 | 7542 | 11 | 6 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8287 | 7543 | 11 | 7 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8288 | 7544 | 11 | 8 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8289 | 7545 | 11 | 9 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8290 | 7546 | 11 | 10 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8291 | 7547 | 11 | 11 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8292 | 7548 | 11 | 12 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8293 | 7549 | 11 | 13 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8294 | 7550 | 11 | 14 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8295 | 7551 | 11 | 15 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8296 | 7552 | 11 | 16 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8297 | 7553 | 11 | 17 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8298 | 7554 | 11 | 18 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8299 | 7555 | 11 | 19 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8300 | 7556 | 11 | 20 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8301 | 7557 | 11 | 21 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8302 | 7558 | 11 | 22 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8303 | 7559 | 11 | 23 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8304 | 7560 | 11 | 24 | 315 | 43415 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8305 | 7561 | 11 | 1 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8306 | 7562 | 11 | 2 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8307 | 7563 | 11 | 3 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8308 | 7564 | 11 | 4 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8309 | 7565 | 11 | 5 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8310 | 7566 | 11 | 6 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8311 | 7567 | 11 | 7 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8312 | 7568 | 11 | 8 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8313 | 7569 | 11 | 9 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8314 | 7570 | 11 | 10 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8315 | 7571 | 11 | 11 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8316 | 7572 | 11 | 12 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8317 | 7573 | 11 | 13 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8318 | 7574 | 11 | 14 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8319 | 7575 | 11 | 15 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8320 | 7576 | 11 | 16 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8321 | 7577 | 11 | 17 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8322 | 7578 | 11 | 18 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8323 | 7579 | 11 | 19 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8324 | 7580 | 11 | 20 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8325 | 7581 | 11 | 21 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8326 | 7582 | 11 | 22 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8327 | 7583 | 11 | 23 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8328 | 7584 | 11 | 24 | 316 | 43416 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8329 | 7585 | 11 | 1 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8330 | 7586 | 11 | 2 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8331 | 7587 | 11 | 3 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8332 | 7588 | 11 | 4 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8333 | 7589 | 11 | 5 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8334 | 7590 | 11 | 6 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8335 | 7591 | 11 | 7 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8336 | 7592 | 11 | 8 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8337 | 7593 | 11 | 9 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8338 | 7594 | 11 | 10 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8339 | 7595 | 11 | 11 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8340 | 7596 | 11 | 12 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8341 | 7597 | 11 | 13 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8342 | 7598 | 11 | 14 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8343 | 7599 | 11 | 15 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8344 | 7600 | 11 | 16 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8345 | 7601 | 11 | 17 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8346 | 7602 | 11 | 18 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8347 | 7603 | 11 | 19 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8348 | 7604 | 11 | 20 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8349 | 7605 | 11 | 21 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8350 | 7606 | 11 | 22 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8351 | 7607 | 11 | 23 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8352 | 7608 | 11 | 24 | 317 | 43417 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8353 | 7609 | 11 | 1 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8354 | 7610 | 11 | 2 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8355 | 7611 | 11 | 3 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8356 | 7612 | 11 | 4 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8357 | 7613 | 11 | 5 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8358 | 7614 | 11 | 6 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8359 | 7615 | 11 | 7 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8360 | 7616 | 11 | 8 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8361 | 7617 | 11 | 9 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8362 | 7618 | 11 | 10 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8363 | 7619 | 11 | 11 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8364 | 7620 | 11 | 12 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8365 | 7621 | 11 | 13 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8366 | 7622 | 11 | 14 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8367 | 7623 | 11 | 15 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8368 | 7624 | 11 | 16 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8369 | 7625 | 11 | 17 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8370 | 7626 | 11 | 18 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8371 | 7627 | 11 | 19 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8372 | 7628 | 11 | 20 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8373 | 7629 | 11 | 21 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8374 | 7630 | 11 | 22 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8375 | 7631 | 11 | 23 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8376 | 7632 | 11 | 24 | 318 | 43418 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8377 | 7633 | 11 | 1 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8378 | 7634 | 11 | 2 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8379 | 7635 | 11 | 3 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8380 | 7636 | 11 | 4 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8381 | 7637 | 11 | 5 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8382 | 7638 | 11 | 6 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8383 | 7639 | 11 | 7 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8384 | 7640 | 11 | 8 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8385 | 7641 | 11 | 9 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8386 | 7642 | 11 | 10 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8387 | 7643 | 11 | 11 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8388 | 7644 | 11 | 12 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8389 | 7645 | 11 | 13 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8390 | 7646 | 11 | 14 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8391 | 7647 | 11 | 15 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8392 | 7648 | 11 | 16 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8393 | 7649 | 11 | 17 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8394 | 7650 | 11 | 18 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8395 | 7651 | 11 | 19 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8396 | 7652 | 11 | 20 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8397 | 7653 | 11 | 21 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8398 | 7654 | 11 | 22 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8399 | 7655 | 11 | 23 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8400 | 7656 | 11 | 24 | 319 | 43419 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8401 | 7657 | 11 | 1 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8402 | 7658 | 11 | 2 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8403 | 7659 | 11 | 3 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8404 | 7660 | 11 | 4 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8405 | 7661 | 11 | 5 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8406 | 7662 | 11 | 6 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8407 | 7663 | 11 | 7 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8408 | 7664 | 11 | 8 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8409 | 7665 | 11 | 9 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8410 | 7666 | 11 | 10 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8411 | 7667 | 11 | 11 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8412 | 7668 | 11 | 12 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8413 | 7669 | 11 | 13 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8414 | 7670 | 11 | 14 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8415 | 7671 | 11 | 15 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8416 | 7672 | 11 | 16 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8417 | 7673 | 11 | 17 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8418 | 7674 | 11 | 18 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8419 | 7675 | 11 | 19 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8420 | 7676 | 11 | 20 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8421 | 7677 | 11 | 21 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8422 | 7678 | 11 | 22 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8423 | 7679 | 11 | 23 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8424 | 7680 | 11 | 24 | 320 | 43420 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8425 | 7681 | 11 | 1 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8426 | 7682 | 11 | 2 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8427 | 7683 | 11 | 3 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8428 | 7684 | 11 | 4 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8429 | 7685 | 11 | 5 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8430 | 7686 | 11 | 6 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8431 | 7687 | 11 | 7 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8432 | 7688 | 11 | 8 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8433 | 7689 | 11 | 9 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8434 | 7690 | 11 | 10 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8435 | 7691 | 11 | 11 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8436 | 7692 | 11 | 12 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8437 | 7693 | 11 | 13 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8438 | 7694 | 11 | 14 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8439 | 7695 | 11 | 15 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8440 | 7696 | 11 | 16 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8441 | 7697 | 11 | 17 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8442 | 7698 | 11 | 18 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8443 | 7699 | 11 | 19 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8444 | 7700 | 11 | 20 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8445 | 7701 | 11 | 21 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8446 | 7702 | 11 | 22 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8447 | 7703 | 11 | 23 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8448 | 7704 | 11 | 24 | 321 | 43421 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8449 | 7705 | 11 | 1 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8450 | 7706 | 11 | 2 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8451 | 7707 | 11 | 3 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8452 | 7708 | 11 | 4 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8453 | 7709 | 11 | 5 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8454 | 7710 | 11 | 6 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8455 | 7711 | 11 | 7 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8456 | 7712 | 11 | 8 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8457 | 7713 | 11 | 9 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8458 | 7714 | 11 | 10 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8459 | 7715 | 11 | 11 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8460 | 7716 | 11 | 12 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8461 | 7717 | 11 | 13 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8462 | 7718 | 11 | 14 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8463 | 7719 | 11 | 15 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8464 | 7720 | 11 | 16 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8465 | 7721 | 11 | 17 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8466 | 7722 | 11 | 18 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8467 | 7723 | 11 | 19 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8468 | 7724 | 11 | 20 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8469 | 7725 | 11 | 21 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8470 | 7726 | 11 | 22 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8471 | 7727 | 11 | 23 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8472 | 7728 | 11 | 24 | 322 | 43422 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8473 | 7729 | 11 | 1 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8474 | 7730 | 11 | 2 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8475 | 7731 | 11 | 3 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8476 | 7732 | 11 | 4 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8477 | 7733 | 11 | 5 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8478 | 7734 | 11 | 6 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8479 | 7735 | 11 | 7 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8480 | 7736 | 11 | 8 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8481 | 7737 | 11 | 9 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8482 | 7738 | 11 | 10 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8483 | 7739 | 11 | 11 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8484 | 7740 | 11 | 12 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8485 | 7741 | 11 | 13 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8486 | 7742 | 11 | 14 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8487 | 7743 | 11 | 15 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8488 | 7744 | 11 | 16 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8489 | 7745 | 11 | 17 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8490 | 7746 | 11 | 18 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8491 | 7747 | 11 | 19 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8492 | 7748 | 11 | 20 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8493 | 7749 | 11 | 21 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8494 | 7750 | 11 | 22 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8495 | 7751 | 11 | 23 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8496 | 7752 | 11 | 24 | 323 | 43423 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8497 | 7753 | 11 | 1 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8498 | 7754 | 11 | 2 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8499 | 7755 | 11 | 3 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8500 | 7756 | 11 | 4 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8501 | 7757 | 11 | 5 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8502 | 7758 | 11 | 6 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8503 | 7759 | 11 | 7 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8504 | 7760 | 11 | 8 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8505 | 7761 | 11 | 9 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8506 | 7762 | 11 | 10 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8507 | 7763 | 11 | 11 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8508 | 7764 | 11 | 12 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8509 | 7765 | 11 | 13 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8510 | 7766 | 11 | 14 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8511 | 7767 | 11 | 15 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8512 | 7768 | 11 | 16 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8513 | 7769 | 11 | 17 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8514 | 7770 | 11 | 18 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8515 | 7771 | 11 | 19 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8516 | 7772 | 11 | 20 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8517 | 7773 | 11 | 21 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8518 | 7774 | 11 | 22 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8519 | 7775 | 11 | 23 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8520 | 7776 | 11 | 24 | 324 | 43424 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8521 | 7777 | 11 | 1 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8522 | 7778 | 11 | 2 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8523 | 7779 | 11 | 3 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8524 | 7780 | 11 | 4 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8525 | 7781 | 11 | 5 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8526 | 7782 | 11 | 6 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8527 | 7783 | 11 | 7 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8528 | 7784 | 11 | 8 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8529 | 7785 | 11 | 9 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8530 | 7786 | 11 | 10 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8531 | 7787 | 11 | 11 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8532 | 7788 | 11 | 12 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8533 | 7789 | 11 | 13 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8534 | 7790 | 11 | 14 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8535 | 7791 | 11 | 15 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8536 | 7792 | 11 | 16 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8537 | 7793 | 11 | 17 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8538 | 7794 | 11 | 18 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8539 | 7795 | 11 | 19 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8540 | 7796 | 11 | 20 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8541 | 7797 | 11 | 21 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8542 | 7798 | 11 | 22 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8543 | 7799 | 11 | 23 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8544 | 7800 | 11 | 24 | 325 | 43425 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8545 | 7801 | 11 | 1 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8546 | 7802 | 11 | 2 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8547 | 7803 | 11 | 3 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8548 | 7804 | 11 | 4 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8549 | 7805 | 11 | 5 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8550 | 7806 | 11 | 6 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8551 | 7807 | 11 | 7 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8552 | 7808 | 11 | 8 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8553 | 7809 | 11 | 9 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8554 | 7810 | 11 | 10 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8555 | 7811 | 11 | 11 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8556 | 7812 | 11 | 12 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8557 | 7813 | 11 | 13 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8558 | 7814 | 11 | 14 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8559 | 7815 | 11 | 15 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8560 | 7816 | 11 | 16 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8561 | 7817 | 11 | 17 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8562 | 7818 | 11 | 18 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8563 | 7819 | 11 | 19 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8564 | 7820 | 11 | 20 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8565 | 7821 | 11 | 21 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8566 | 7822 | 11 | 22 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8567 | 7823 | 11 | 23 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8568 | 7824 | 11 | 24 | 326 | 43426 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8569 | 7825 | 11 | 1 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8570 | 7826 | 11 | 2 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8571 | 7827 | 11 | 3 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8572 | 7828 | 11 | 4 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8573 | 7829 | 11 | 5 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8574 | 7830 | 11 | 6 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8575 | 7831 | 11 | 7 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8576 | 7832 | 11 | 8 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8577 | 7833 | 11 | 9 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8578 | 7834 | 11 | 10 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8579 | 7835 | 11 | 11 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8580 | 7836 | 11 | 12 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8581 | 7837 | 11 | 13 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8582 | 7838 | 11 | 14 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8583 | 7839 | 11 | 15 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8584 | 7840 | 11 | 16 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8585 | 7841 | 11 | 17 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8586 | 7842 | 11 | 18 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8587 | 7843 | 11 | 19 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8588 | 7844 | 11 | 20 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8589 | 7845 | 11 | 21 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8590 | 7846 | 11 | 22 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8591 | 7847 | 11 | 23 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8592 | 7848 | 11 | 24 | 327 | 43427 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8593 | 7849 | 11 | 1 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8594 | 7850 | 11 | 2 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8595 | 7851 | 11 | 3 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8596 | 7852 | 11 | 4 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8597 | 7853 | 11 | 5 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8598 | 7854 | 11 | 6 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8599 | 7855 | 11 | 7 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8600 | 7856 | 11 | 8 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8601 | 7857 | 11 | 9 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8602 | 7858 | 11 | 10 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8603 | 7859 | 11 | 11 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8604 | 7860 | 11 | 12 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8605 | 7861 | 11 | 13 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8606 | 7862 | 11 | 14 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8607 | 7863 | 11 | 15 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8608 | 7864 | 11 | 16 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8609 | 7865 | 11 | 17 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8610 | 7866 | 11 | 18 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8611 | 7867 | 11 | 19 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8612 | 7868 | 11 | 20 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8613 | 7869 | 11 | 21 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8614 | 7870 | 11 | 22 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8615 | 7871 | 11 | 23 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8616 | 7872 | 11 | 24 | 328 | 43428 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8617 | 7873 | 11 | 1 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8618 | 7874 | 11 | 2 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8619 | 7875 | 11 | 3 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8620 | 7876 | 11 | 4 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8621 | 7877 | 11 | 5 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8622 | 7878 | 11 | 6 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8623 | 7879 | 11 | 7 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8624 | 7880 | 11 | 8 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8625 | 7881 | 11 | 9 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8626 | 7882 | 11 | 10 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8627 | 7883 | 11 | 11 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8628 | 7884 | 11 | 12 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8629 | 7885 | 11 | 13 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8630 | 7886 | 11 | 14 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8631 | 7887 | 11 | 15 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8632 | 7888 | 11 | 16 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8633 | 7889 | 11 | 17 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8634 | 7890 | 11 | 18 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8635 | 7891 | 11 | 19 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8636 | 7892 | 11 | 20 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8637 | 7893 | 11 | 21 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8638 | 7894 | 11 | 22 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8639 | 7895 | 11 | 23 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8640 | 7896 | 11 | 24 | 329 | 43429 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8641 | 7897 | 11 | 1 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8642 | 7898 | 11 | 2 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8643 | 7899 | 11 | 3 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8644 | 7900 | 11 | 4 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8645 | 7901 | 11 | 5 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8646 | 7902 | 11 | 6 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8647 | 7903 | 11 | 7 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8648 | 7904 | 11 | 8 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8649 | 7905 | 11 | 9 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8650 | 7906 | 11 | 10 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8651 | 7907 | 11 | 11 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8652 | 7908 | 11 | 12 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8653 | 7909 | 11 | 13 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8654 | 7910 | 11 | 14 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8655 | 7911 | 11 | 15 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8656 | 7912 | 11 | 16 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8657 | 7913 | 11 | 17 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8658 | 7914 | 11 | 18 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8659 | 7915 | 11 | 19 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8660 | 7916 | 11 | 20 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8661 | 7917 | 11 | 21 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8662 | 7918 | 11 | 22 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8663 | 7919 | 11 | 23 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8664 | 7920 | 11 | 24 | 330 | 43430 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8665 | 7921 | 11 | 1 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8666 | 7922 | 11 | 2 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8667 | 7923 | 11 | 3 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8668 | 7924 | 11 | 4 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8669 | 7925 | 11 | 5 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8670 | 7926 | 11 | 6 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8671 | 7927 | 11 | 7 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8672 | 7928 | 11 | 8 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8673 | 7929 | 11 | 9 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8674 | 7930 | 11 | 10 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8675 | 7931 | 11 | 11 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8676 | 7932 | 11 | 12 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8677 | 7933 | 11 | 13 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8678 | 7934 | 11 | 14 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8679 | 7935 | 11 | 15 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8680 | 7936 | 11 | 16 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8681 | 7937 | 11 | 17 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8682 | 7938 | 11 | 18 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8683 | 7939 | 11 | 19 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8684 | 7940 | 11 | 20 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8685 | 7941 | 11 | 21 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8686 | 7942 | 11 | 22 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8687 | 7943 | 11 | 23 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8688 | 7944 | 11 | 24 | 331 | 43431 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8689 | 7945 | 11 | 1 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8690 | 7946 | 11 | 2 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8691 | 7947 | 11 | 3 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8692 | 7948 | 11 | 4 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8693 | 7949 | 11 | 5 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8694 | 7950 | 11 | 6 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8695 | 7951 | 11 | 7 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8696 | 7952 | 11 | 8 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8697 | 7953 | 11 | 9 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8698 | 7954 | 11 | 10 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8699 | 7955 | 11 | 11 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8700 | 7956 | 11 | 12 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8701 | 7957 | 11 | 13 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8702 | 7958 | 11 | 14 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8703 | 7959 | 11 | 15 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8704 | 7960 | 11 | 16 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8705 | 7961 | 11 | 17 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8706 | 7962 | 11 | 18 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8707 | 7963 | 11 | 19 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8708 | 7964 | 11 | 20 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8709 | 7965 | 11 | 21 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8710 | 7966 | 11 | 22 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8711 | 7967 | 11 | 23 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8712 | 7968 | 11 | 24 | 332 | 43432 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8713 | 7969 | 11 | 1 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8714 | 7970 | 11 | 2 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8715 | 7971 | 11 | 3 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8716 | 7972 | 11 | 4 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8717 | 7973 | 11 | 5 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8718 | 7974 | 11 | 6 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8719 | 7975 | 11 | 7 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8720 | 7976 | 11 | 8 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8721 | 7977 | 11 | 9 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8722 | 7978 | 11 | 10 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8723 | 7979 | 11 | 11 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8724 | 7980 | 11 | 12 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8725 | 7981 | 11 | 13 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8726 | 7982 | 11 | 14 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8727 | 7983 | 11 | 15 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8728 | 7984 | 11 | 16 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8729 | 7985 | 11 | 17 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8730 | 7986 | 11 | 18 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8731 | 7987 | 11 | 19 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8732 | 7988 | 11 | 20 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8733 | 7989 | 11 | 21 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8734 | 7990 | 11 | 22 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8735 | 7991 | 11 | 23 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8736 | 7992 | 11 | 24 | 333 | 43433 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8737 | 7993 | 11 | 1 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8738 | 7994 | 11 | 2 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8739 | 7995 | 11 | 3 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8740 | 7996 | 11 | 4 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8741 | 7997 | 11 | 5 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8742 | 7998 | 11 | 6 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8743 | 7999 | 11 | 7 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8744 | 8000 | 11 | 8 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8745 | 8001 | 11 | 9 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8746 | 8002 | 11 | 10 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8747 | 8003 | 11 | 11 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8748 | 8004 | 11 | 12 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8749 | 8005 | 11 | 13 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8750 | 8006 | 11 | 14 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8751 | 8007 | 11 | 15 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8752 | 8008 | 11 | 16 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8753 | 8009 | 11 | 17 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8754 | 8010 | 11 | 18 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8755 | 8011 | 11 | 19 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8756 | 8012 | 11 | 20 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8757 | 8013 | 11 | 21 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8758 | 8014 | 11 | 22 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8759 | 8015 | 11 | 23 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8760 | 8016 | 11 | 24 | 334 | 43434 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8761 | 8017 | 12 | 1 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8762 | 8018 | 12 | 2 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8763 | 8019 | 12 | 3 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8764 | 8020 | 12 | 4 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8765 | 8021 | 12 | 5 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8766 | 8022 | 12 | 6 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8767 | 8023 | 12 | 7 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8768 | 8024 | 12 | 8 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8769 | 8025 | 12 | 9 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8770 | 8026 | 12 | 10 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8771 | 8027 | 12 | 11 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8772 | 8028 | 12 | 12 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8773 | 8029 | 12 | 13 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8774 | 8030 | 12 | 14 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8775 | 8031 | 12 | 15 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8776 | 8032 | 12 | 16 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8777 | 8033 | 12 | 17 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8778 | 8034 | 12 | 18 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8779 | 8035 | 12 | 19 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8780 | 8036 | 12 | 20 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8781 | 8037 | 12 | 21 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8782 | 8038 | 12 | 22 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8783 | 8039 | 12 | 23 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8784 | 8040 | 12 | 24 | 335 | 43435 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8785 | 8041 | 12 | 1 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8786 | 8042 | 12 | 2 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8787 | 8043 | 12 | 3 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8788 | 8044 | 12 | 4 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8789 | 8045 | 12 | 5 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8790 | 8046 | 12 | 6 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8791 | 8047 | 12 | 7 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8792 | 8048 | 12 | 8 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8793 | 8049 | 12 | 9 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8794 | 8050 | 12 | 10 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8795 | 8051 | 12 | 11 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8796 | 8052 | 12 | 12 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8797 | 8053 | 12 | 13 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8798 | 8054 | 12 | 14 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8799 | 8055 | 12 | 15 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8800 | 8056 | 12 | 16 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8801 | 8057 | 12 | 17 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8802 | 8058 | 12 | 18 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8803 | 8059 | 12 | 19 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8804 | 8060 | 12 | 20 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8805 | 8061 | 12 | 21 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8806 | 8062 | 12 | 22 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8807 | 8063 | 12 | 23 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8808 | 8064 | 12 | 24 | 336 | 43436 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8809 | 8065 | 12 | 1 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8810 | 8066 | 12 | 2 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8811 | 8067 | 12 | 3 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8812 | 8068 | 12 | 4 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8813 | 8069 | 12 | 5 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8814 | 8070 | 12 | 6 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8815 | 8071 | 12 | 7 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8816 | 8072 | 12 | 8 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8817 | 8073 | 12 | 9 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8818 | 8074 | 12 | 10 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8819 | 8075 | 12 | 11 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8820 | 8076 | 12 | 12 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8821 | 8077 | 12 | 13 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8822 | 8078 | 12 | 14 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8823 | 8079 | 12 | 15 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8824 | 8080 | 12 | 16 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8825 | 8081 | 12 | 17 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8826 | 8082 | 12 | 18 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8827 | 8083 | 12 | 19 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8828 | 8084 | 12 | 20 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8829 | 8085 | 12 | 21 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8830 | 8086 | 12 | 22 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8831 | 8087 | 12 | 23 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8832 | 8088 | 12 | 24 | 337 | 43437 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8833 | 8089 | 12 | 1 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8834 | 8090 | 12 | 2 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8835 | 8091 | 12 | 3 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8836 | 8092 | 12 | 4 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8837 | 8093 | 12 | 5 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8838 | 8094 | 12 | 6 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8839 | 8095 | 12 | 7 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8840 | 8096 | 12 | 8 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8841 | 8097 | 12 | 9 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8842 | 8098 | 12 | 10 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8843 | 8099 | 12 | 11 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8844 | 8100 | 12 | 12 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8845 | 8101 | 12 | 13 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8846 | 8102 | 12 | 14 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8847 | 8103 | 12 | 15 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8848 | 8104 | 12 | 16 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8849 | 8105 | 12 | 17 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8850 | 8106 | 12 | 18 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8851 | 8107 | 12 | 19 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8852 | 8108 | 12 | 20 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8853 | 8109 | 12 | 21 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8854 | 8110 | 12 | 22 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8855 | 8111 | 12 | 23 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8856 | 8112 | 12 | 24 | 338 | 43438 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8857 | 8113 | 12 | 1 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8858 | 8114 | 12 | 2 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8859 | 8115 | 12 | 3 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8860 | 8116 | 12 | 4 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8861 | 8117 | 12 | 5 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8862 | 8118 | 12 | 6 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8863 | 8119 | 12 | 7 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8864 | 8120 | 12 | 8 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8865 | 8121 | 12 | 9 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8866 | 8122 | 12 | 10 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8867 | 8123 | 12 | 11 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8868 | 8124 | 12 | 12 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8869 | 8125 | 12 | 13 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8870 | 8126 | 12 | 14 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8871 | 8127 | 12 | 15 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8872 | 8128 | 12 | 16 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8873 | 8129 | 12 | 17 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8874 | 8130 | 12 | 18 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8875 | 8131 | 12 | 19 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8876 | 8132 | 12 | 20 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8877 | 8133 | 12 | 21 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8878 | 8134 | 12 | 22 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8879 | 8135 | 12 | 23 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8880 | 8136 | 12 | 24 | 339 | 43439 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8881 | 8137 | 12 | 1 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8882 | 8138 | 12 | 2 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8883 | 8139 | 12 | 3 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8884 | 8140 | 12 | 4 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8885 | 8141 | 12 | 5 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8886 | 8142 | 12 | 6 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8887 | 8143 | 12 | 7 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8888 | 8144 | 12 | 8 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8889 | 8145 | 12 | 9 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8890 | 8146 | 12 | 10 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8891 | 8147 | 12 | 11 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8892 | 8148 | 12 | 12 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8893 | 8149 | 12 | 13 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8894 | 8150 | 12 | 14 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8895 | 8151 | 12 | 15 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8896 | 8152 | 12 | 16 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8897 | 8153 | 12 | 17 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8898 | 8154 | 12 | 18 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8899 | 8155 | 12 | 19 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8900 | 8156 | 12 | 20 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8901 | 8157 | 12 | 21 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8902 | 8158 | 12 | 22 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8903 | 8159 | 12 | 23 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8904 | 8160 | 12 | 24 | 340 | 43440 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8905 | 8161 | 12 | 1 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8906 | 8162 | 12 | 2 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8907 | 8163 | 12 | 3 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8908 | 8164 | 12 | 4 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8909 | 8165 | 12 | 5 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8910 | 8166 | 12 | 6 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8911 | 8167 | 12 | 7 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8912 | 8168 | 12 | 8 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8913 | 8169 | 12 | 9 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8914 | 8170 | 12 | 10 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8915 | 8171 | 12 | 11 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8916 | 8172 | 12 | 12 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8917 | 8173 | 12 | 13 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8918 | 8174 | 12 | 14 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8919 | 8175 | 12 | 15 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8920 | 8176 | 12 | 16 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8921 | 8177 | 12 | 17 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8922 | 8178 | 12 | 18 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8923 | 8179 | 12 | 19 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8924 | 8180 | 12 | 20 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8925 | 8181 | 12 | 21 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8926 | 8182 | 12 | 22 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8927 | 8183 | 12 | 23 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8928 | 8184 | 12 | 24 | 341 | 43441 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8929 | 8185 | 12 | 1 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8930 | 8186 | 12 | 2 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8931 | 8187 | 12 | 3 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8932 | 8188 | 12 | 4 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8933 | 8189 | 12 | 5 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8934 | 8190 | 12 | 6 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8935 | 8191 | 12 | 7 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8936 | 8192 | 12 | 8 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8937 | 8193 | 12 | 9 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8938 | 8194 | 12 | 10 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8939 | 8195 | 12 | 11 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8940 | 8196 | 12 | 12 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8941 | 8197 | 12 | 13 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8942 | 8198 | 12 | 14 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8943 | 8199 | 12 | 15 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8944 | 8200 | 12 | 16 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8945 | 8201 | 12 | 17 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8946 | 8202 | 12 | 18 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8947 | 8203 | 12 | 19 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8948 | 8204 | 12 | 20 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8949 | 8205 | 12 | 21 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8950 | 8206 | 12 | 22 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8951 | 8207 | 12 | 23 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8952 | 8208 | 12 | 24 | 342 | 43442 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8953 | 8209 | 12 | 1 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8954 | 8210 | 12 | 2 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8955 | 8211 | 12 | 3 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8956 | 8212 | 12 | 4 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8957 | 8213 | 12 | 5 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8958 | 8214 | 12 | 6 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8959 | 8215 | 12 | 7 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8960 | 8216 | 12 | 8 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8961 | 8217 | 12 | 9 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8962 | 8218 | 12 | 10 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8963 | 8219 | 12 | 11 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8964 | 8220 | 12 | 12 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8965 | 8221 | 12 | 13 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8966 | 8222 | 12 | 14 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8967 | 8223 | 12 | 15 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8968 | 8224 | 12 | 16 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8969 | 8225 | 12 | 17 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8970 | 8226 | 12 | 18 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8971 | 8227 | 12 | 19 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8972 | 8228 | 12 | 20 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8973 | 8229 | 12 | 21 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8974 | 8230 | 12 | 22 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8975 | 8231 | 12 | 23 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8976 | 8232 | 12 | 24 | 343 | 43443 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8977 | 8233 | 12 | 1 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8978 | 8234 | 12 | 2 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8979 | 8235 | 12 | 3 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8980 | 8236 | 12 | 4 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8981 | 8237 | 12 | 5 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8982 | 8238 | 12 | 6 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8983 | 8239 | 12 | 7 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8984 | 8240 | 12 | 8 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8985 | 8241 | 12 | 9 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8986 | 8242 | 12 | 10 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8987 | 8243 | 12 | 11 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8988 | 8244 | 12 | 12 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8989 | 8245 | 12 | 13 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8990 | 8246 | 12 | 14 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8991 | 8247 | 12 | 15 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8992 | 8248 | 12 | 16 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8993 | 8249 | 12 | 17 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8994 | 8250 | 12 | 18 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8995 | 8251 | 12 | 19 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8996 | 8252 | 12 | 20 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8997 | 8253 | 12 | 21 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8998 | 8254 | 12 | 22 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 8999 | 8255 | 12 | 23 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9000 | 8256 | 12 | 24 | 344 | 43444 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9001 | 8257 | 12 | 1 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9002 | 8258 | 12 | 2 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9003 | 8259 | 12 | 3 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9004 | 8260 | 12 | 4 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9005 | 8261 | 12 | 5 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9006 | 8262 | 12 | 6 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9007 | 8263 | 12 | 7 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9008 | 8264 | 12 | 8 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9009 | 8265 | 12 | 9 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9010 | 8266 | 12 | 10 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9011 | 8267 | 12 | 11 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9012 | 8268 | 12 | 12 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9013 | 8269 | 12 | 13 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9014 | 8270 | 12 | 14 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9015 | 8271 | 12 | 15 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9016 | 8272 | 12 | 16 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9017 | 8273 | 12 | 17 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9018 | 8274 | 12 | 18 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9019 | 8275 | 12 | 19 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9020 | 8276 | 12 | 20 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9021 | 8277 | 12 | 21 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9022 | 8278 | 12 | 22 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9023 | 8279 | 12 | 23 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9024 | 8280 | 12 | 24 | 345 | 43445 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9025 | 8281 | 12 | 1 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9026 | 8282 | 12 | 2 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9027 | 8283 | 12 | 3 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9028 | 8284 | 12 | 4 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9029 | 8285 | 12 | 5 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9030 | 8286 | 12 | 6 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9031 | 8287 | 12 | 7 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9032 | 8288 | 12 | 8 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9033 | 8289 | 12 | 9 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9034 | 8290 | 12 | 10 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9035 | 8291 | 12 | 11 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9036 | 8292 | 12 | 12 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9037 | 8293 | 12 | 13 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9038 | 8294 | 12 | 14 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9039 | 8295 | 12 | 15 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9040 | 8296 | 12 | 16 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9041 | 8297 | 12 | 17 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9042 | 8298 | 12 | 18 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9043 | 8299 | 12 | 19 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9044 | 8300 | 12 | 20 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9045 | 8301 | 12 | 21 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9046 | 8302 | 12 | 22 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9047 | 8303 | 12 | 23 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9048 | 8304 | 12 | 24 | 346 | 43446 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9049 | 8305 | 12 | 1 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9050 | 8306 | 12 | 2 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9051 | 8307 | 12 | 3 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9052 | 8308 | 12 | 4 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9053 | 8309 | 12 | 5 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9054 | 8310 | 12 | 6 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9055 | 8311 | 12 | 7 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9056 | 8312 | 12 | 8 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9057 | 8313 | 12 | 9 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9058 | 8314 | 12 | 10 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9059 | 8315 | 12 | 11 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9060 | 8316 | 12 | 12 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9061 | 8317 | 12 | 13 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9062 | 8318 | 12 | 14 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9063 | 8319 | 12 | 15 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9064 | 8320 | 12 | 16 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9065 | 8321 | 12 | 17 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9066 | 8322 | 12 | 18 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9067 | 8323 | 12 | 19 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9068 | 8324 | 12 | 20 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9069 | 8325 | 12 | 21 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9070 | 8326 | 12 | 22 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9071 | 8327 | 12 | 23 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9072 | 8328 | 12 | 24 | 347 | 43447 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9073 | 8329 | 12 | 1 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9074 | 8330 | 12 | 2 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9075 | 8331 | 12 | 3 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9076 | 8332 | 12 | 4 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9077 | 8333 | 12 | 5 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9078 | 8334 | 12 | 6 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9079 | 8335 | 12 | 7 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9080 | 8336 | 12 | 8 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9081 | 8337 | 12 | 9 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9082 | 8338 | 12 | 10 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9083 | 8339 | 12 | 11 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9084 | 8340 | 12 | 12 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9085 | 8341 | 12 | 13 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9086 | 8342 | 12 | 14 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9087 | 8343 | 12 | 15 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9088 | 8344 | 12 | 16 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9089 | 8345 | 12 | 17 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9090 | 8346 | 12 | 18 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9091 | 8347 | 12 | 19 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9092 | 8348 | 12 | 20 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9093 | 8349 | 12 | 21 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9094 | 8350 | 12 | 22 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9095 | 8351 | 12 | 23 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9096 | 8352 | 12 | 24 | 348 | 43448 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9097 | 8353 | 12 | 1 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9098 | 8354 | 12 | 2 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9099 | 8355 | 12 | 3 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9100 | 8356 | 12 | 4 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9101 | 8357 | 12 | 5 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9102 | 8358 | 12 | 6 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9103 | 8359 | 12 | 7 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9104 | 8360 | 12 | 8 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9105 | 8361 | 12 | 9 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9106 | 8362 | 12 | 10 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9107 | 8363 | 12 | 11 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9108 | 8364 | 12 | 12 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9109 | 8365 | 12 | 13 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9110 | 8366 | 12 | 14 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9111 | 8367 | 12 | 15 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9112 | 8368 | 12 | 16 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9113 | 8369 | 12 | 17 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9114 | 8370 | 12 | 18 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9115 | 8371 | 12 | 19 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9116 | 8372 | 12 | 20 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9117 | 8373 | 12 | 21 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9118 | 8374 | 12 | 22 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9119 | 8375 | 12 | 23 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9120 | 8376 | 12 | 24 | 349 | 43449 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9121 | 8377 | 12 | 1 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9122 | 8378 | 12 | 2 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9123 | 8379 | 12 | 3 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9124 | 8380 | 12 | 4 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9125 | 8381 | 12 | 5 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9126 | 8382 | 12 | 6 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9127 | 8383 | 12 | 7 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9128 | 8384 | 12 | 8 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9129 | 8385 | 12 | 9 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9130 | 8386 | 12 | 10 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9131 | 8387 | 12 | 11 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9132 | 8388 | 12 | 12 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9133 | 8389 | 12 | 13 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9134 | 8390 | 12 | 14 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9135 | 8391 | 12 | 15 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9136 | 8392 | 12 | 16 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9137 | 8393 | 12 | 17 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9138 | 8394 | 12 | 18 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9139 | 8395 | 12 | 19 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9140 | 8396 | 12 | 20 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9141 | 8397 | 12 | 21 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9142 | 8398 | 12 | 22 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9143 | 8399 | 12 | 23 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9144 | 8400 | 12 | 24 | 350 | 43450 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9145 | 8401 | 12 | 1 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9146 | 8402 | 12 | 2 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9147 | 8403 | 12 | 3 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9148 | 8404 | 12 | 4 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9149 | 8405 | 12 | 5 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9150 | 8406 | 12 | 6 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9151 | 8407 | 12 | 7 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9152 | 8408 | 12 | 8 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9153 | 8409 | 12 | 9 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9154 | 8410 | 12 | 10 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9155 | 8411 | 12 | 11 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9156 | 8412 | 12 | 12 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9157 | 8413 | 12 | 13 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9158 | 8414 | 12 | 14 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9159 | 8415 | 12 | 15 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9160 | 8416 | 12 | 16 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9161 | 8417 | 12 | 17 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9162 | 8418 | 12 | 18 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9163 | 8419 | 12 | 19 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9164 | 8420 | 12 | 20 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9165 | 8421 | 12 | 21 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9166 | 8422 | 12 | 22 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9167 | 8423 | 12 | 23 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9168 | 8424 | 12 | 24 | 351 | 43451 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9169 | 8425 | 12 | 1 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9170 | 8426 | 12 | 2 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9171 | 8427 | 12 | 3 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9172 | 8428 | 12 | 4 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9173 | 8429 | 12 | 5 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9174 | 8430 | 12 | 6 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9175 | 8431 | 12 | 7 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9176 | 8432 | 12 | 8 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9177 | 8433 | 12 | 9 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9178 | 8434 | 12 | 10 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9179 | 8435 | 12 | 11 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9180 | 8436 | 12 | 12 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9181 | 8437 | 12 | 13 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9182 | 8438 | 12 | 14 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9183 | 8439 | 12 | 15 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9184 | 8440 | 12 | 16 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9185 | 8441 | 12 | 17 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9186 | 8442 | 12 | 18 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9187 | 8443 | 12 | 19 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9188 | 8444 | 12 | 20 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9189 | 8445 | 12 | 21 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9190 | 8446 | 12 | 22 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9191 | 8447 | 12 | 23 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9192 | 8448 | 12 | 24 | 352 | 43452 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9193 | 8449 | 12 | 1 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9194 | 8450 | 12 | 2 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9195 | 8451 | 12 | 3 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9196 | 8452 | 12 | 4 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9197 | 8453 | 12 | 5 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9198 | 8454 | 12 | 6 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9199 | 8455 | 12 | 7 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9200 | 8456 | 12 | 8 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9201 | 8457 | 12 | 9 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9202 | 8458 | 12 | 10 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9203 | 8459 | 12 | 11 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9204 | 8460 | 12 | 12 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9205 | 8461 | 12 | 13 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9206 | 8462 | 12 | 14 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9207 | 8463 | 12 | 15 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9208 | 8464 | 12 | 16 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9209 | 8465 | 12 | 17 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9210 | 8466 | 12 | 18 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9211 | 8467 | 12 | 19 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9212 | 8468 | 12 | 20 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9213 | 8469 | 12 | 21 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9214 | 8470 | 12 | 22 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9215 | 8471 | 12 | 23 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9216 | 8472 | 12 | 24 | 353 | 43453 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9217 | 8473 | 12 | 1 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9218 | 8474 | 12 | 2 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9219 | 8475 | 12 | 3 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9220 | 8476 | 12 | 4 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9221 | 8477 | 12 | 5 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9222 | 8478 | 12 | 6 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9223 | 8479 | 12 | 7 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9224 | 8480 | 12 | 8 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9225 | 8481 | 12 | 9 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9226 | 8482 | 12 | 10 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9227 | 8483 | 12 | 11 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9228 | 8484 | 12 | 12 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9229 | 8485 | 12 | 13 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9230 | 8486 | 12 | 14 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9231 | 8487 | 12 | 15 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9232 | 8488 | 12 | 16 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9233 | 8489 | 12 | 17 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9234 | 8490 | 12 | 18 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9235 | 8491 | 12 | 19 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9236 | 8492 | 12 | 20 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9237 | 8493 | 12 | 21 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9238 | 8494 | 12 | 22 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9239 | 8495 | 12 | 23 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9240 | 8496 | 12 | 24 | 354 | 43454 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9241 | 8497 | 12 | 1 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9242 | 8498 | 12 | 2 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9243 | 8499 | 12 | 3 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9244 | 8500 | 12 | 4 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9245 | 8501 | 12 | 5 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9246 | 8502 | 12 | 6 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9247 | 8503 | 12 | 7 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9248 | 8504 | 12 | 8 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9249 | 8505 | 12 | 9 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9250 | 8506 | 12 | 10 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9251 | 8507 | 12 | 11 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9252 | 8508 | 12 | 12 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9253 | 8509 | 12 | 13 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9254 | 8510 | 12 | 14 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9255 | 8511 | 12 | 15 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9256 | 8512 | 12 | 16 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9257 | 8513 | 12 | 17 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9258 | 8514 | 12 | 18 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9259 | 8515 | 12 | 19 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9260 | 8516 | 12 | 20 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9261 | 8517 | 12 | 21 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9262 | 8518 | 12 | 22 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9263 | 8519 | 12 | 23 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9264 | 8520 | 12 | 24 | 355 | 43455 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9265 | 8521 | 12 | 1 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9266 | 8522 | 12 | 2 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9267 | 8523 | 12 | 3 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9268 | 8524 | 12 | 4 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9269 | 8525 | 12 | 5 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9270 | 8526 | 12 | 6 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9271 | 8527 | 12 | 7 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9272 | 8528 | 12 | 8 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9273 | 8529 | 12 | 9 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9274 | 8530 | 12 | 10 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9275 | 8531 | 12 | 11 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9276 | 8532 | 12 | 12 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9277 | 8533 | 12 | 13 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9278 | 8534 | 12 | 14 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9279 | 8535 | 12 | 15 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9280 | 8536 | 12 | 16 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9281 | 8537 | 12 | 17 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9282 | 8538 | 12 | 18 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9283 | 8539 | 12 | 19 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9284 | 8540 | 12 | 20 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9285 | 8541 | 12 | 21 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9286 | 8542 | 12 | 22 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9287 | 8543 | 12 | 23 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9288 | 8544 | 12 | 24 | 356 | 43456 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9289 | 8545 | 12 | 1 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9290 | 8546 | 12 | 2 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9291 | 8547 | 12 | 3 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9292 | 8548 | 12 | 4 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9293 | 8549 | 12 | 5 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9294 | 8550 | 12 | 6 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9295 | 8551 | 12 | 7 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9296 | 8552 | 12 | 8 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9297 | 8553 | 12 | 9 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9298 | 8554 | 12 | 10 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9299 | 8555 | 12 | 11 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9300 | 8556 | 12 | 12 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9301 | 8557 | 12 | 13 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9302 | 8558 | 12 | 14 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9303 | 8559 | 12 | 15 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9304 | 8560 | 12 | 16 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9305 | 8561 | 12 | 17 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9306 | 8562 | 12 | 18 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9307 | 8563 | 12 | 19 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9308 | 8564 | 12 | 20 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9309 | 8565 | 12 | 21 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9310 | 8566 | 12 | 22 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9311 | 8567 | 12 | 23 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9312 | 8568 | 12 | 24 | 357 | 43457 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9313 | 8569 | 12 | 1 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9314 | 8570 | 12 | 2 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9315 | 8571 | 12 | 3 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9316 | 8572 | 12 | 4 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9317 | 8573 | 12 | 5 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9318 | 8574 | 12 | 6 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9319 | 8575 | 12 | 7 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9320 | 8576 | 12 | 8 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9321 | 8577 | 12 | 9 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9322 | 8578 | 12 | 10 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9323 | 8579 | 12 | 11 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9324 | 8580 | 12 | 12 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9325 | 8581 | 12 | 13 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9326 | 8582 | 12 | 14 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9327 | 8583 | 12 | 15 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9328 | 8584 | 12 | 16 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9329 | 8585 | 12 | 17 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9330 | 8586 | 12 | 18 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9331 | 8587 | 12 | 19 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9332 | 8588 | 12 | 20 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9333 | 8589 | 12 | 21 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9334 | 8590 | 12 | 22 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9335 | 8591 | 12 | 23 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9336 | 8592 | 12 | 24 | 358 | 43458 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9337 | 8593 | 12 | 1 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9338 | 8594 | 12 | 2 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9339 | 8595 | 12 | 3 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9340 | 8596 | 12 | 4 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9341 | 8597 | 12 | 5 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9342 | 8598 | 12 | 6 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9343 | 8599 | 12 | 7 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9344 | 8600 | 12 | 8 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9345 | 8601 | 12 | 9 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9346 | 8602 | 12 | 10 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9347 | 8603 | 12 | 11 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9348 | 8604 | 12 | 12 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9349 | 8605 | 12 | 13 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9350 | 8606 | 12 | 14 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9351 | 8607 | 12 | 15 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9352 | 8608 | 12 | 16 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9353 | 8609 | 12 | 17 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9354 | 8610 | 12 | 18 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9355 | 8611 | 12 | 19 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9356 | 8612 | 12 | 20 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9357 | 8613 | 12 | 21 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9358 | 8614 | 12 | 22 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9359 | 8615 | 12 | 23 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9360 | 8616 | 12 | 24 | 359 | 43459 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9361 | 8617 | 12 | 1 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9362 | 8618 | 12 | 2 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9363 | 8619 | 12 | 3 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9364 | 8620 | 12 | 4 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9365 | 8621 | 12 | 5 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9366 | 8622 | 12 | 6 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9367 | 8623 | 12 | 7 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9368 | 8624 | 12 | 8 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9369 | 8625 | 12 | 9 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9370 | 8626 | 12 | 10 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9371 | 8627 | 12 | 11 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9372 | 8628 | 12 | 12 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9373 | 8629 | 12 | 13 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9374 | 8630 | 12 | 14 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9375 | 8631 | 12 | 15 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9376 | 8632 | 12 | 16 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9377 | 8633 | 12 | 17 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9378 | 8634 | 12 | 18 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9379 | 8635 | 12 | 19 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9380 | 8636 | 12 | 20 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9381 | 8637 | 12 | 21 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9382 | 8638 | 12 | 22 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9383 | 8639 | 12 | 23 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9384 | 8640 | 12 | 24 | 360 | 43460 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9385 | 8641 | 12 | 1 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9386 | 8642 | 12 | 2 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9387 | 8643 | 12 | 3 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9388 | 8644 | 12 | 4 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9389 | 8645 | 12 | 5 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9390 | 8646 | 12 | 6 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9391 | 8647 | 12 | 7 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9392 | 8648 | 12 | 8 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9393 | 8649 | 12 | 9 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9394 | 8650 | 12 | 10 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9395 | 8651 | 12 | 11 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9396 | 8652 | 12 | 12 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9397 | 8653 | 12 | 13 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9398 | 8654 | 12 | 14 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9399 | 8655 | 12 | 15 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9400 | 8656 | 12 | 16 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9401 | 8657 | 12 | 17 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9402 | 8658 | 12 | 18 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9403 | 8659 | 12 | 19 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9404 | 8660 | 12 | 20 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9405 | 8661 | 12 | 21 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9406 | 8662 | 12 | 22 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9407 | 8663 | 12 | 23 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9408 | 8664 | 12 | 24 | 361 | 43461 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9409 | 8665 | 12 | 1 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9410 | 8666 | 12 | 2 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9411 | 8667 | 12 | 3 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9412 | 8668 | 12 | 4 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9413 | 8669 | 12 | 5 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9414 | 8670 | 12 | 6 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9415 | 8671 | 12 | 7 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9416 | 8672 | 12 | 8 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9417 | 8673 | 12 | 9 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9418 | 8674 | 12 | 10 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9419 | 8675 | 12 | 11 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9420 | 8676 | 12 | 12 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9421 | 8677 | 12 | 13 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9422 | 8678 | 12 | 14 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9423 | 8679 | 12 | 15 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9424 | 8680 | 12 | 16 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9425 | 8681 | 12 | 17 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9426 | 8682 | 12 | 18 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9427 | 8683 | 12 | 19 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9428 | 8684 | 12 | 20 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9429 | 8685 | 12 | 21 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9430 | 8686 | 12 | 22 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9431 | 8687 | 12 | 23 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9432 | 8688 | 12 | 24 | 362 | 43462 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9433 | 8689 | 12 | 1 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9434 | 8690 | 12 | 2 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9435 | 8691 | 12 | 3 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9436 | 8692 | 12 | 4 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9437 | 8693 | 12 | 5 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9438 | 8694 | 12 | 6 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9439 | 8695 | 12 | 7 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9440 | 8696 | 12 | 8 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9441 | 8697 | 12 | 9 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9442 | 8698 | 12 | 10 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9443 | 8699 | 12 | 11 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9444 | 8700 | 12 | 12 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9445 | 8701 | 12 | 13 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9446 | 8702 | 12 | 14 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9447 | 8703 | 12 | 15 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9448 | 8704 | 12 | 16 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9449 | 8705 | 12 | 17 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9450 | 8706 | 12 | 18 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9451 | 8707 | 12 | 19 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9452 | 8708 | 12 | 20 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9453 | 8709 | 12 | 21 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9454 | 8710 | 12 | 22 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9455 | 8711 | 12 | 23 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9456 | 8712 | 12 | 24 | 363 | 43463 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9457 | 8713 | 12 | 1 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9458 | 8714 | 12 | 2 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9459 | 8715 | 12 | 3 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9460 | 8716 | 12 | 4 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9461 | 8717 | 12 | 5 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9462 | 8718 | 12 | 6 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9463 | 8719 | 12 | 7 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9464 | 8720 | 12 | 8 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9465 | 8721 | 12 | 9 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9466 | 8722 | 12 | 10 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9467 | 8723 | 12 | 11 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9468 | 8724 | 12 | 12 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9469 | 8725 | 12 | 13 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9470 | 8726 | 12 | 14 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9471 | 8727 | 12 | 15 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9472 | 8728 | 12 | 16 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9473 | 8729 | 12 | 17 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9474 | 8730 | 12 | 18 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9475 | 8731 | 12 | 19 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9476 | 8732 | 12 | 20 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9477 | 8733 | 12 | 21 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9478 | 8734 | 12 | 22 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9479 | 8735 | 12 | 23 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9480 | 8736 | 12 | 24 | 364 | 43464 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9481 | 8737 | 12 | 1 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9482 | 8738 | 12 | 2 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9483 | 8739 | 12 | 3 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9484 | 8740 | 12 | 4 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9485 | 8741 | 12 | 5 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9486 | 8742 | 12 | 6 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9487 | 8743 | 12 | 7 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9488 | 8744 | 12 | 8 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9489 | 8745 | 12 | 9 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9490 | 8746 | 12 | 10 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9491 | 8747 | 12 | 11 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9492 | 8748 | 12 | 12 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9493 | 8749 | 12 | 13 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9494 | 8750 | 12 | 14 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9495 | 8751 | 12 | 15 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9496 | 8752 | 12 | 16 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9497 | 8753 | 12 | 17 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9498 | 8754 | 12 | 18 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 3 | 2 | 20 | 27 | 25 | 60 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9499 | 8755 | 12 | 19 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9500 | 8756 | 12 | 20 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9501 | 8757 | 12 | 21 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9502 | 8758 | 12 | 22 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9503 | 8759 | 12 | 23 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0
|  | 9504 | 8760 | 12 | 24 | 365 | 43465 | WRK | 0.03125 | 3 | 3 | 3 | 0 | 2 | 20 | 27 | 0 | 100 | 0.3075 | 0 | 4.1667 | 0 | 0

## CalcShad
To be completed

## AdaptW
See sheet adaptW for general explanation on this sheet with input data
Key choices:
Select adaptive element number (id) from library | 5 | from library, see below
Select operation type: MAN, MOT, AUT | AUT
Select space type: RES, OFF | OFF | <<< shd match >>> | BESTEST600 | (see sheet Input_p)
LIBRARY OF ADAPTIVE ELEMENTS (max. 12) with properties for each key state
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
|  |  | Extension status 0 (retracted) |  |  |  | Extension status 1 |  |  |  |  | Extension status 2 |  |  |  |  | Extension status 3
Number (id) | Description | Type | Uw;Wadapti;sti | gw;Wadapti;sti | τe;w;Wadapti;sti | τvis;w;Wadapti;sti | Descr. | Uw;Wadapti;sti | gw;Wadapti;sti | τe;w;Wadapti;sti | τvis;w;Wadapti;sti | Descr. | Uw;Wadapti;sti | gw;Wadapti;sti | τe;w;Wadapti;sti | τvis;w;Wadapti;sti | Descr. | Uw;Wadapti;sti | gw;Wadapti;sti | τe;w;Wadapti;sti | τvis;w;Wadapti;sti
1 | SG-EXRBLD | ExRoChr | 5.809 | 0.884 | 0.87 | 0.905 | simply extended | 3.269 | 0.114 | 0.02 | 0.014 | as status 1 | 3.269 | 0.114 | 0.02 | 0.014 | as status 1 | 3.269 | 0.114 | 0.02 | 0.014
2 | SG-EXVBLD | ExVen | 5.809 | 0.884 | 0.87 | 0.905 | slats 0 degr. | 3.784 | 0.231 | 0.18 | 0.212 | slats 45 degr. | 3.72 | 0.132 | 0.08 | 0.1 | slats 80 degr. | 3.507 | 0.066 | 0.02 | 0.023
3 | SG-INVBLD | InVen | 5.809 | 0.884 | 0.87 | 0.905 | slats 0 degr. | 4.685 | 0.548 | 0.3 | 0.361 | slats 45 degr. | 4.499 | 0.38 | 0.16 | 0.192 | slats 80 degr. | 4.15 | 0.24 | 0.04 | 0.047
4 | DG-EXRBLD | ExRoChr | 1.063 | 0.653 | 0.58 | 0.814 | simply extended | 0.9 | 0.04 | 0.01 | 0.012 | as status 1 | 0.9 | 0.04 | 0.01 | 0.012 | as status 1 | 0.9 | 0.04 | 0.01 | 0.012
5 | DG-EXVBLD | ExVen | 1.063 | 0.653 | 0.58 | 0.814 | slats 0 degr. | 0.936 | 0.142 | 0.11 | 0.178 | slats 45 degr. | 0.931 | 0.074 | 0.06 | 0.085 | slats 80 degr. | 0.914 | 0.03 | 0.01 | 0.02
6 | DG-INVBLD | InVen | 1.063 | 0.653 | 0.58 | 0.814 | slats 0 degr. | 0.978 | 0.478 | 0.21 | 0.327 | slats 45 degr. | 0.966 | 0.384 | 0.12 | 0.182 | slats 80 degr. | 0.941 | 0.294 | 0.03 | 0.046
7 | SCG-EXRBLD | ExRoChr | 0.984 | 0.332 | 0.31 | 0.699 | simply extended | 0.837 | 0.03 | 0 | 0.01 | as status 1 | 0.837 | 0.03 | 0 | 0.01 | as status 1 | 0.837 | 0.03 | 0 | 0.01
8 | SCG-EXVBLD | ExVen | 0.984 | 0.332 | 0.31 | 0.699 | slats 0 degr. | 0.869 | 0.086 | 0.06 | 0.152 | slats 45 degr. | 0.863 | 0.046 | 0.03 | 0.073 | slats 80 degr. | 0.849 | 0.022 | 0.01 | 0.017
9 | SCG-INVBLD | InVen | 0.984 | 0.332 | 0.31 | 0.699 | slats 0 degr. | 0.906 | 0.228 | 0.12 | 0.284 | slats 45 degr. | 0.895 | 0.171 | 0.07 | 0.161 | slats 80 degr. | 0.873 | 0.117 | 0.02 | 0.041
10 | TRG-EXRBLD | ExRoChr | 0.727 | 0.526 | 0.45 | 0.742 | simply extended | 0.645 | 0.029 | 0.01 | 0.01 | as status 1 | 0.645 | 0.029 | 0.01 | 0.01 | as status 1 | 0.645 | 0.029 | 0.01 | 0.01
11 | TRG-EXVBLD | ExVen | 0.727 | 0.526 | 0.45 | 0.742 | slats 0 degr. | 0.664 | 0.111 | 0.08 | 0.152 | slats 45 degr. | 0.661 | 0.058 | 0.04 | 0.073 | slats 80 degr. | 0.652 | 0.021 | 0.01 | 0.017
12 | TRG-INVBLD | InVen | 0.727 | 0.526 | 0.45 | 0.742 | slats 0 degr. | 0.686 | 0.391 | 0.17 | 0.297 | slats 45 degr. | 0.68 | 0.324 | 0.1 | 0.172 | slats 80 degr. | 0.666 | 0.258 | 0.03 | 0.044